## yorktrcastructureSearchResult
INSPECTION YEAR | SITE ID | MUNICIPALITY | WATERSHED | WATERCOURSE | INSPECTION DATE | INSPECTION START TIME | INSPECTION END TIME | INSPECTED BY(STAFF1) | INSPECTED BY(STAFF2) | INSPECTION TYPE | INFRASTRUCTURE TYPE | PIPE SEGMENT | NAD83 E | NAD83 N | N/S STREET | E/W STREET | ACCESS NOTES | PROPERTY OWNERSHIP | SOIL SERIES | SOIL TYPE | INFRASTRUCTURE CROSSING TYPE | INFRASTRUCTURE CROSSING LOCATION | DESIGN DRAWING NUMBER | CONTRACT NUMBER | ACTIVE PROJECT SITE | CANDIDATE PROJECT SITE | MAINTENANCE PRIORITY | MAINTENANCE STATUS COMMENTS | TRCA PRIORITY RANKING | YORK PRIORITY RANKING | INSPECTION FREQUENCY | QC'D BY | STATUS | REASON INACTIVE | RECOMMENDED FOR SURVEY(INTERSECTION) | AS-BUILT DEPTH OF COVER(M) | SURVEYED DEPTH OF COVER(M) | DATE OF SURVEY(INTERSECTION) | RECOMMENDED FOR SURVEY(PROXIMITY) | AS-BUILT CLOSEST DISTANCE TO BANK(M) | CURRENT CLOSEST DISTANCE TO BANK(M) | CURRENT CLOSEST DISTANCE TYPE | DATE OF SURVEY(PROXIMITY) | EROSION HAZARD SCORE | PRIMARY BED MATERIAL | SECONDARY BED MATERIAL | PRIMARY LEFT BANK MATERIAL | SECONDARY LEFT BANK MATERIAL | PRIMARY RIGHT BANK MATERIAL | SECONDARY RIGHT BANK MATERIAL | PERCENT VEGETATED | PREDOMINANT VEGETATION TYPE | WIDTH AT BANKFULL(M) | MAX DEPTH AT BANKFULL(M) | WIDTH TO MAX DEPTH RATIO | WATER DEPTH(M) | ISLAND | BARS | POOLS | RIFFLES | DOWNCUTTING | WIDENING | LATERAL MIGRATION | DEPOSITION | EDDYING | EXPOSED CLAY | EXPOSED BEDROCK | GULLING/SURFACE RUNOFF | SEEPAGE | UNDERCUT BANKS | FAILING/FAILED TREES | DEBRIS JAMS | MASS MOVEMENT/SLOPE INSTABILITY | OTHER | OTHER COMMENTS | INSPECTION COMMENTS | PIN 1 DISTANCE(M) | PIN 2 DISTANCE(M) | PIN 3 DISTANCE(M) | PIN 1 NAD83 E | PIN 1 NAD83 N | PIN 2 NAD83 E | PIN 2 NAD83 N | PIN 3 NAD83 E | PIN 3 NAD83 N | InspectionReason
2011 | I-151 | Markham | Don River | German Mills Creek (DR) | 2011-09-21 | 13:24 | 13:40 | MJ | RB | Intersection | Sanitary Main (Gravity) | MHLC183 - MHLC184 | 630858.1 | 4852418.8 | LESLIE STREET | STEELES AVE | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years | DC | Active |  | No | 2.1 |  |  | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | N/A | Boulders (265mm +) | N/A | 61-90 | Mixed | 9 | 2 | 4.5 | 0.77 | D | U | A | U&D | No | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | BANK SCOUR | ON THE RIGHT BANK (OUTER MEANDER) A FIELDSTONE REVETMENT PROVIDES BANK PROTECTION IN THE AREA OF THE CROSSING. BANK PROTECTION LOOKS FAIRLY NEW AND HAS NO DEFICIENCIES. ON THE LEFT BANK THERE IS A 9.4M BANK SCOUR UNDERCUTTING THE BANKTHAT EXTENDS U/S OF THE CROSSING SITE. TWO OUTFALLS ARE PRESENT, ONE ON EACH BANK IMMEDIATELY D/S OF THE CROSSING AREA. SANITARY MAIN IS NOT CURRENTLY EXPOSED. LOW PRIORITY AS THE RIGHT BANK PROTECTION IS IN EXCELLENT CONDITION, BUT BED MAY DOWNCUT ALONG THE THALWEG IN THE FUTURE. THE AS-BUILT SHOWS 2.1 M OF PROTECTION.
2012 | I-151 | Markham | Don River | German Mills Creek (DR) | 2012-06-22 | 10:10 | 10:40 | MK | RP | Intersection | Sanitary Main (Gravity) | MHLC183 - MHLC184 | 630858.1 | 4852418.8 | LESLIE STREET | STEELES AVE | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years | DC | Active |  | No | 2.1 |  |  | No | [5 empty] | Cobbles (64 - 256 mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Densely Vegetated | Cobbles (64 - 256 mm) | Gravel (2 - 64 mm) | 31-60 | Grasses/Forbs | 8 | 1.75 | 4.57 | 0.8 | D | D | A | U&D | No | No | No | No | Yes | No | No | No | No | No | No | No | Yes | Yes | EROSION SCAR | SECTIONS OF THE LEFT BANK HAVE COLLAPSED INTO THE CHANNEL CREATING ISLANDS LOCATED ALONG THE OUTER MEANDER D/S OF CROSSING. A COBBLE AND BOULDER REVETMENT LINES THE RIGHT BANK AT THE CROSSING AND IS IN GOOD CONDITION. U/S OF THE CROSSING AND REVETMENT THE RIGHT BANK IS SCOURED (15 M LONG BY 0.8 M HIGH AND 0.3 DEEP). AN OUTFALL ON THE LEFT BANK DIRECTLY D/S OF THE CROSSING CAUSING SOME POOLING AND EDDYING AT THE END OF THE SPILLWAY WHERE THE BANK CUTS IN FURTHER TO THE LEFT. AN EROSION SCAR ~10 M IS LOCATED ON THE LEFT BANK WHERE MASS MOVEMENT HAS OCURRED, SCOUR IS DIRECTLY D/S OF THE CROSSING. SOME POOLING DIRECTLY OVER CROSSING AREA. SAFETY ISSUE AT OUTFALL AS GATE IS LEFT OPEN. LOW PRIORITY ASSIGNED AS DEPTH OF COVER (AS-BUILT) IS 2.1 M AND NO SIGNS OF DOWNCUTTING OBSERVED.
2014 | I-151 | Markham | Don River | German Mills Creek (DR) | 2014-06-18 | 11:18 | 11:48 | OT |  | Intersection | Sanitary Main (Gravity) | MHLC183 - MHLC184 | 630858.1 | 4852418.8 | LESLIE STREET | STEELES AVE | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years | SL | Active |  | No | 2.1 |  |  | No | [5 empty] | Cobbles (64 - 256 mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | N/A | Boulders (265mm +) | Sand (< 2mm) | 31-60 | Mixed | 9.4 | 1.55 | 6.06 | 0.48 | D | D | A | D | Yes | No | No | No | No | No | No | No | No | No | No | No | Yes | Yes | BANK SCOUR | THE SANITARY MAIN CROSSES BENEATH A POOL. THE RIGHT BANK IS SCOURING U/S OF THE BOULDER REVETMENT (SCOUR DIMENSIONS: 15 M LENGTH, 0.8 M HEIGHT, 0.3 DEPTH). CHANNEL BED APPEARS TO BE DOWNCUTTING U/S OF CROSSING NEAR THE RIGHT BANK (APPROXIMATE DOWNCUT DEPTH OF 0.5 M). A 10 M SCOUR IS LOCATED ON THE LEFT BANK IN AREA OF CROSSING. LOW PRIORITY ASSIGNED AS DEPTH OF COVER (AS-BUILT) IS 2.1 M WITH ONLY MINOR SIGNS OF DOWNCUTTING AT TIME OF INSPECTION.
2016 | I-151 | Markham | Don River | German Mills Creek (DR) | 2016-06-14 | 9:14 | 9:35 | KY | JDa | Intersection | Sanitary Main (Gravity) | MHLC183 - MHLC184 | 630858.1 | 4852418.8 | LESLIE STREET | STEELES AVE | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years | NB | Active |  | No | 2.1 |  |  | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Boulders (265mm +) | Cobbles (64 - 256 mm) | 61-90 | Grasses/Forbs | 10 | 1.51 | 6.62 | 0.17 | N | N | U | D | Yes | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | BANK SCOURING | THE SANITARY MAIN CROSSES BENEATH A POOL. THE RIGHT BANK IS SCOURING U/S OF THE BOULDER REVETMENT (SCOUR DIMENSIONS: 15 M LENGTH, 0.8 M HEIGHT, 0.3 DEPTH). UNDERCUTTING DIRECTLY D/S OF THE OUTFALL (0.49 M IN DEPTH). CHANNEL BED APPEARS TO BE DOWNCUTTING U/S OF CROSSING NEAR THE RIGHT BANK (1.14 M IN DEPTH). THE LEFT BANK IS SCOURING IN THE AREA OF CROSSING (SCOUR DIMENSIONS: 8.4 M LENGTH, 1.70 M HEIGHT, AND 1.85 M WIDTH). LOW PRIORITY ASSIGNED AS DEPTH OF COVER (AS-BUILT) IS 2.1 M WITH ONLY MINOR SIGNS OF DOWNCUTTING ADJACENT TO INTERSECTION AT TIME OF INSPECTION.
2018 | I-151 | Markham | Don River | German Mills Creek (DR) | 2018-06-05 | 12:04 | 12:14 | HC | OT | Intersection | Sanitary Main (Gravity) | MHLC183 - MHLC184 | 630858.1 | 4852418.8 | LESLIE STREET | STEELES AVE | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years |  | Active |  | No | 2.1 |  |  | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Boulders (265mm +) | Cobbles (64 - 256 mm) | 61-90 | Grasses/Forbs | 10.2 | 2.11 | 4.83 | 0.94 | A | U&D | U&D | A | Yes | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | BANK SCOUR | THE SANITARY MAIN (GRAVITY) CROSSES BENEATH A POOL IN THE WATERCOURSE. THE RIGHT BANK IS SCOURING U/S OF THE BOULDER REVETMENT (SCOUR DIMENSIONS: 15 M LENGTH, 0.8 M HEIGHT, 0.3 DEPTH). CHANNEL BED APPEARS TO BE DOWNCUTTING U/S OF CROSSING NEAR THE RIGHT BANK (0.94 M IN DEPTH). THE LEFT BANK IS SCOURING IN THE AREA OF CROSSING (SCOUR DIMENSIONS: 10 M LENGTH, 1.40 M HEIGHT, AND 1 M WIDTH, 0.1 M UNDERCUTTING). THERE ARE SIGNS OF RECENT SLUMPING OF LEFT BANK. LOW PRIORITY ASSIGNED AS DEPTH OF COVER (AS-BUILT) IS 2.1 M WITH ONLY MINOR SIGNS OF DOWNCUTTING ADJACENT TO INTERSECTION AT TIME OF INSPECTION.
2021 | I-151 | Markham | Don River | German Mills Creek (DR) | 2021-07-14 | 9:50 | 10:15 | RR | SCa | Intersection | Sanitary Main (Gravity) | MHLC183 - MHLC184 | 630858.1 | 4852418.8 | LESLIE STREET | STEELES AVE | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years |  | Active |  | No | 2.1 |  |  | No | [5 empty] | Sand (< 2mm) | N/A | Bedrock | Sand (< 2mm) | Sand (< 2mm) | Densely Vegetated | 0-30 | Grasses/Forbs |  |  |  |  | N | U | A | D | Yes | No | No | No | No | No | No | No | No | No | No | No | No | Yes | outflanking, toe erosion | The sanitary main (gravity) crosses diagonally beneath a pool in the watercourse. Conditions since previous inspection have slightly changed. Right bank scour is still evident although large pieces of land have slumped off and have settled at the middle of the scour (once bare section) and are providing added protection and stability to the scour. The left bank scour is still evident although staff could not take measurements due to dense vegetation overgrowth around the scour. Downcutting was noted along the right bank u/s of the crossing measuring 0.98 m (average water depth 0.25 m). Boulders protect the toe of the right bank of the watercourse and they experiencing signs of minor displacement. Minor to moderate slumping is occurring along the right bank and pieces of slumped land have settled onto the top of the toe protection. Some vegetation growth is occurring between the boulders as well. An outfall is located adjacent to the crossing on the left bank. The right wing wall is experiencing minor outflanking and some toe erosion along the bank closest to the sanitary line.
2023 | I-151 | Markham | Don River | German Mills Creek (DR) | 2023-07-07 | 11:30 | 0:10 | KLa | ALo | Intersection | Sanitary Main (Gravity) | MHLC183 - MHLC184 | 630858.1 | 4852418.8 | LESLIE STREET | STEELES AVE | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years |  | Active |  | No | 2.1 |  |  | No | [5 empty] | Cobbles (64 - 256 mm) | Sand (< 2mm) | Densely Vegetated | Cobbles (64 - 256 mm) | Cobbles (64 - 256 mm) | Densely Vegetated | 0-30 | Grasses/Forbs | 18 | 1.66 | 10.84 | 0.3 | N | D | U | A | Yes | No | No | No | No | No | No | No | No | Yes | Yes | No | No | Yes | Spalling | Minor changes have occurred since the pervious site inspection; area of downcutting u/s is no longer present and downcutting is now present at the d/s limit of the site. The sanitary main (gravity) crosses diagonally beneath a pool in the watercourse. Adjacent to the area of the crossing a outfall is located along the left bank and debris buildup is occurring at the grate of the outfall. The spillway and right wingwall are experiencing moderate spalling and area of toe erosion is no longer present. Another outfall is present d/s on the right bank and appears in good condition. The right and left banks are protected by a cobble revetment in the area of the crossing. The material that slumped from the right bank scour in the pervious report is now re-vegetated and scour is not observed due to vegetation. A scour is present at the d/s of the crossing along the left bank and measures 9 m in length, 1.26 m in width and 1.18 m in height and undercut 0.48 m at the crest with slumping throughout the scour. An undermined tree of 1.10 m is present at the midsection of the scour with exposed roots. Downcutting of 0.41 m is present at the d/s limit adjacent to the undermined tree.
2011 | I-152 | Markham | Don River | German Mills Creek (DR) | 2011-08-12 | 12:35 | 13:01 | SN | MJ | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  | DC | Active |  | No | 1.67 |  |  | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Densely Vegetated | 61-90 | Grasses/Forbs | 10.7 | 1.5 | 7.13 | 0.31 | N | A | A | D | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | No |  | THE SANITARY MAIN CROSSES BENEATH A STRAIGHT SECTION OF A VERY SINUOUS SECTION OF THE WATERCOURSE. THE CHANNEL BED IS COMPOSED OF LOOSE GRAVEL AND SAND. THERE IS A 50 M EROSION SCAR ON THE LEFT BANK. Â MASS MOVEMENT APPEARS TO BE RECENT. Â THERE IS A FALLEN TREE IN THE CHANNEL ADJACENT TO THE LEFT BANK WHICH SHOULD BE REMOVED TO PREVENT DEBRIS ACCUMULATION. A MANHOLE IS LOCATED 3.1 M FROM THE LEFT BANK AND MAY BE AT RISK IN THE FUTURE DUE TO LATERAL MIGRATION. ALTHOUGH INFRASTRUCTURE IS NOT CURRENTLY AT RISK DUE TO DOWNCUTTING, THE SANITARY MH MAY BE AT RISK Â IF THE BANK CONTINUES TO ERODE THEREFORE HIGH PRIORITY ASSIGNED.
2012 | I-152 | Markham | Don River | German Mills Creek (DR) | 2012-06-26 | 9:55 | 10:17 | CR | RP | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 3 |  |  | DC | Active |  | No | 1.67 |  |  | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Densely Vegetated | 61-90 | Mixed | 9.4 | 0.8 | 11.75 | 0.18 | N | A | U&D | A | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | No | Yes | Yes | BANK SCOUR | THE SANITARY MAIN CROSSES BENEATH A RIFFLE IN A STRAIGHT SECTION OF A VERY SINUOUS PART OF THE WATERCOURSE. THE CHANNEL MEANDERS U/S AND D/S OF THE CROSSING. AT THE U/S MEANDER A RIP RAP REVETMENT ARMOURS THE LEFT BANK. GRADUAL SCOURING BEGINS AT THE D/S LIMIT OF THE LEFT BANK REVETMENT. SCOUR LENGTH IS ~50 M AND HEIGHT IS 1.0 M. THE LEFT BANK IS UNDERCUT 0.4 M EXPOSING TREE ROOTS. THE PRESENCE OF LEANING TREES INDICATE THE LEFT BANK MAY BE AT FUTURE RISK. MASS MOVEMENT APPEARS TO BE RECENT. GRADUAL MIGRATION IS OCCURING NEAR A MANHOLE 3.1 M FROM THE LEFT BANK CREST - UNCHANGED FROM THE 2011 INSPECTION. THE RIGHT BANK IN THE CROSSING AREA APPEARS TO BE STABLE AND ABUNDANT WITH VEGETATION. NO APPARENT DOWNCUTTING OF THE BED. MEDIUM PRIORITY DUE TO PROXIMITY OF MANHOLE TO EROSION SCAR.
2013 | I-152 | Markham | Don River | German Mills Creek (DR) | 2013-05-22 | 11:19 | 11:41 | MK | CP | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  | SL | Active |  | No | 1.67 |  |  | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Densely Vegetated | 61-90 | Mixed | 11.2 | 1.6 | 7 | 0.36 | N | N | U&D | A | No | Yes | No | No | No | No | No | No | No | Yes | Yes | No | Yes | Yes | TENSION CRACKS | THE SANITARY MAIN CROSSES BENEATH A RIFFLE. THE LEFT BANK AT THE CROSSING IS ERODING AT HIGH FLOW. THE LEFT BANK HAS RECEDED NEARLY 2 M SINCE 2012 IN AREA OF THE MANHOLE. THE MANHOLE IS CURRENTLY LOCATED 1.0 M FROM THE SCOUR. NO APPARENT DOWNCUTTING OBSERVED ON THE CHANNEL BED AT CROSSING. LEFT BANK SCOUR MEASURES APPROXIMATELY 50 M IN LENGTH WITH A HEIGHT OF 1.5 M. SIGNIFICANT UNDERCUTTING OF THE SCOUR CREST (1.5 M) DIRECTLY ADJACENT TO MANHOLE. LEANING AND FAILING TREES THROUGHOUT THE RIPARIAN ZONE OF LEFT BANK. HIGH PRIORITY DUE TO PROGRESSIVE ADVANCEMENT OF SCOUR TOWARD MANHOLE AND SIGNS OF RECENT MOVEMENT.
2014 | I-152 | Markham | Don River | German Mills Creek (DR) | 2014-06-17 | 10:09 | 10:33 | JS | OT | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  | SL | Active |  | No | 1.67 | 1.54 | 2014-05-23 | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | N/A | 61-90 | Mixed | 11.5 | 1.02 | 11.27 | 0.07 | N | D | U | D | No | Yes | No | No | No | No | No | No | No | Yes | Yes | No | No | No |  | THE 2014 SURVEYED DEPTH OF COVER IS 1.5 M OVER THE CROSSING. MAJOR SCOURING AND UNDERCUTTING ALONG THE LEFT BANK NEAR MANHOLE (LC-09) (SCOUR DIMENSIONS: > 50 M LENGTH, 1.5 M HEIGHT, 1.2 M WIDTH). UNDERCUT DEPTH IS 0.5 M. THE BANK ADJACENT TO MANHOLE HAS RECEDED MORE THAN 3 M SINCE 2012. THE MANHOLE IS CURRENTLY LOCATED 1 M FROM THE SCOUR AT THE CLOSEST POINT. NUMEROUS TREES GROWING ALONG THE TOP OF SCOUR IS LEANING, UNDERMINED AND AT RISK OF FAILURE. HIGH PRIORITY ASSIGNED DUE TO RISK TO MANHOLE AND PROGRESSIVE BANK EROSION IN THIS AREA.
2014 | I-152 | Markham | Don River | German Mills Creek (DR) | 2014-08-12 | 12:37 | 12:56 | OT | JS | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  | SL | Active |  | No | 1.67 |  |  | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | N/A | 61-90 | Mixed |  |  |  | 0.21 | N | N | A | D | No | No | Yes | No | No | No | No | No | No | Yes | Yes | No | Yes | Yes | BANK SCOUR | Site reinspection following storm events late July to early August 2014. No signs of downcutting since last inspection in area of crossing; the 2014 surveyed depth of cover is 1.5 m (1.7 m as-built). No change in distance from manhole to the north bank since the last inspection (1 m). However, there has been significant loss of bank immediately south of the manhole due to bank caving and failed trees. As a result of this recent movement, there is currently a 0.3 m void on the south side of the concrete chimney adjacent to a leaning tree. The manhole is located 0.8 m from the bank south of the manhole (approx. 1.5 m decrease since site was surveyed in May of this year). Recent movement is observed upstream and downstream of the crossing on the left bank with numerous undermined and failed trees along the crest. Priority remains high due to the risk to the manhole at the crossing. (Note: Manhole found east of MH09 is just a discarded frame and cover.)
2015 | I-152 | Markham | Don River | German Mills Creek (DR) | 2015-05-20 | 10:35 | 10:57 | DM | OT | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  | SL | Active |  | No | 1.67 | 1.61 | 2015-10-19 | No | [5 empty] | Gravel (2 - 64 mm) | Sand (< 2mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 61-90 | Mixed | 13 | 1.38 | 9.42 | 0.25 | N | N | U | D | No | Yes | No | No | No | No | No | No | No | Yes | No | No | Yes | No |  | THE 2015 SURVEYED DEPTH OF COVER IS 1.6 M. NO SIGNS OF DOWNCUTTING AT TIME OF INSPECTION. A MAJOR SCOUR ON THE LEFT BANK IS THREATENING A SANITARY MANHOLE (LC-09) (SCOUR DIMENSIONS: >50 M LENGTH, 1.5 M HEIGHT, 1.2 M WIDTH). RECENT BANK SLUMPING OBSERVED NEAR THE MANHOLE. THE MANHOLE IS CURRENTLY LOCATED 1 M FROM THE NORTH BANK SCOUR AND 0.5 M FROM THE SOUTH BANK SCOUR AT THE CLOSEST POINT. NUMEROUS UNDERMINED TREES GROWING ALONG THE CREST OF SCOUR. HIGH PRIORITY ASSIGNED DUE TO THE CLOSE PROXIMITY OF MANHOLE TO SCOUR.
2016 | I-152 | Markham | Don River | German Mills Creek (DR) | 2016-06-10 | 11:54 | 0:13 | OT | KY | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  | SL | Active |  | No | 1.67 |  |  | No | [5 empty] | Gravel (2 - 64 mm) | Sand (< 2mm) | Sand (< 2mm) | N/A | Sand (< 2mm) | N/A | 61-90 | Mixed | 12.51 | 1.44 | 8.69 | 0.29 | N | N | U | D | Yes | No | Yes | No | No | No | No | No | No | Yes | Yes | No | Yes | Yes | BANK SCOUR | THE 2015 SURVEYED DEPTH OF COVER IS 1.6 M (1.7 M AS-BUILT). MAJOR SCOURING ON THE LEFT BANK IS THREATENING A SANITARY MANHOLE (SCOUR DIMENSIONS: >50 M LENGTH, 1.5 M HEIGHT, 1.2 M WIDTH). MINOR DOWNCUTTING ON BED NEAR THE LEFT BANK IN AREA OF CROSSING. RECENT BANK SLUMPING OBSERVED NEAR THE MANHOLE (UNDERCUT BY 0.5 M). THE MANHOLE IS CURRENTLY LOCATED 1 M FROM THE SCOUR (NORTH OF MANHOLE) AND 0.5 M FROM THE SCOUR (SOUTH OF MANHOLE). NUMEROUS UNDERMINED TREES GROWING ALONG THE SCOUR CREST ARE AT RISK OF FAILURE. HIGH PRIORITY ASSIGNED DUE TO THE RISK TO MANHOLE.
2017 | I-152 | Markham | Don River | German Mills Creek (DR) | 2017-05-12 | 12:06 | 12:22 | KY | OT | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  | JSP | Active |  | No | 1.67 |  |  | No | [5 empty] | Sand (< 2mm) | Cobbles (64 - 256 mm) | Sand (< 2mm) | Cobbles (64 - 256 mm) | Sand (< 2mm) | Silt | 61-90 | Mixed | 11.6 | 1.48 | 7.84 | 0.66 | N | D | A | U&D | Yes | No | No | No | No | No | No | No | No | Yes | Yes | No | Yes | Yes | BANK SCOUR | THE 2015 SURVEYED DEPTH OF COVER IS 1.6 M (1.7 M AS-BUILT). MAJOR SCOURING ON THE LEFT BANK IS THREATENING A SANITARY MANHOLE (SCOUR DIMENSIONS: >50 M LENGTH, 1.5 M HEIGHT, 1.2 M WIDTH). MINOR DOWNCUTTING ON BED NEAR THE LEFT BANK IN AREA OF CROSSING (DEPTH: 0.66 M). RECENT BANK SLUMPING OF SCOUR OBSERVED D/S OF THE MANHOLE (UNDERCUT BY 0.5 M). THE MANHOLE IS CURRENTLY LOCATED 0.5 M FROM SCOUR ON THE SOUTH SIDE AND 1 M FROM A SCOUR ON THE NORTH SIDE. THERE ARE NUMEROUS UNDERMINED TREES GROWING ALONG THE SCOUR CREST AND THEY ARE AT HIGH RISK OF FAILURE. HIGH PRIORITY ASSIGNED DUE TO THE RISK TO MANHOLE.
2017 | I-152 | Markham | Don River | German Mills Creek (DR) | 2017-06-28 | 11:36 | 11:48 | OT | RC | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  | JSP | Active |  | No | 1.67 |  |  | No | [36 empty] | **POST STORM INSPECTION: SMALL DIAMETER TREE ALONG THE CENTRE OF THE CHANNEL IN AREA OF CROSSING AND COULD CONTRIBUTE TO DOWNCUTTING AND/OR DEBRIS BUILDUP. DISTANCE FROM MANHOLE TO NORTHERN BANK RECEDED BY 0.1 M SINCE LAST INSPECTION. SEE PREVIOUS INSPECTION FOR MORE COMMENTS. | bar: N N N N to No Yes No Yes
2018 | I-152 | Markham | Don River | German Mills Creek (DR) | 2018-04-06 | 10:30 | 11:00 | OT | RC | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 |  |  | No | [5 empty] | Sand (< 2mm) | Cobbles (64 - 256 mm) | Sand (< 2mm) | Cobbles (64 - 256 mm) | Sand (< 2mm) | Silt | 31-60 | Mixed | 12.2 | 1.6 | 7.63 | 0.5 | N | A | U | A | Yes | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | BANK SCOUR | THE 2015 SURVEYED DEPTH OF COVER IS 1.6 M (1.7 M AS-BUILT). MAJOR SCOURING ON THE LEFT BANK IS THREATENING A SANITARY MANHOLE (SCOUR DIMENSIONS: >50 M LENGTH, 1.5 M HEIGHT, 1.2 M WIDTH). MINOR DOWNCUTTING ON BED NEAR THE LEFT BANK IN AREA OF CROSSING (DEPTH: 0.66 M). BANK IS SLUMPING IMMEDIATELY D/S OF THE MANHOLE (UNDERCUT BY 0.5 M). THE MANHOLE IS CURRENTLY LOCATED 0.5 M FROM SCOUR ON THE SOUTH SIDE AND 0.9 M FROM A SCOUR ON THE NORTH SIDE. THE SOUTH SIDE OF THE MANHOLE IS EXPOSED (EXPOSED DIMENSIONS: 1 M LENGTH, 0.3 DEPTH, 0.4 M WIDTH) AND IT IS UNDERCUT BY 0.4 M. THERE ARE NUMEROUS UNDERMINED TREES GROWING ALONG THE SCOUR CREST AND THEY ARE AT HIGH RISK OF FAILURE. HIGH PRIORITY ASSIGNED DUE TO THE RISK TO MANHOLE.
2018 | I-152 | Markham | Don River | German Mills Creek (DR) | 2018-04-18 | 10:40 | 10:50 | OT | DG | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 |  |  | No | [5 empty] | Sand (< 2mm) | Cobbles (64 - 256 mm) | Sand (< 2mm) | Cobbles (64 - 256 mm) | Sand (< 2mm) | Silt | 0-30 | Mixed |  |  |  |  | N | N | U&D | A | No | No | No | No | No | No | No | No | No | No | No | No | No | No |  | POST STORM INSPECTION, NO CHANGES OBSERVED SINCE PREVIOUS INSPECTION. THE 2015 SURVEYED DEPTH OF COVER IS 1.6 M (1.7 M AS-BUILT). MAJOR SCOURING ON THE LEFT BANK IS THREATENING A SANITARY MANHOLE (SCOUR DIMENSIONS: >50 M LENGTH, 1.5 M HEIGHT, 1.2 M WIDTH). THE MANHOLE IS 0.9 M FROM THE SCOUR ON THE NORTH SIDE AND 0.5 M FROM SCOUR ON THE SOUTH SIDE. THE SOUTH SIDE OF THE MANHOLE CHIMNEY IS EXPOSED (EXPOSED DIMENSIONS: 1 M LENGTH, 0.3 DEPTH, 0.4 M WIDTH) AND IT IS UNDERCUT BY 0.4 M. HIGH PRIORITY ASSIGNED AS THE NORTH AND SOUTH SIDE OF THE MANHOLE IS SCOURING, PUTTING THE MANHOLE AT RISK.
2018 | I-152 | Markham | Don River | German Mills Creek (DR) | 2018-07-10 | 10:50 | 11:09 | HC | OT | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 | 1.55 | 2018-07-18 | No | [5 empty] | Sand (< 2mm) | Cobbles (64 - 256 mm) | Sand (< 2mm) | Cobbles (64 - 256 mm) | Sand (< 2mm) | Silt | 0-30 | Mixed | 11.2 | 1.62 | 6.91 | 0.19 | D | D | A | U&D | Yes | No | No | No | No | No | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR,TOE EROSION | **POST STORM INSPECTION** THE 2018 SURVEYED DEPTH OF COVER IS 1.55 M (1.7 M AS-BUILT). FALLEN TREE IS FOUND ON THE U/S SECTION OF CROSSING CLOSER TO THE RIGHT BANK. THE TREE APPEARS TO CAUSE DOWNCUTTING WITH (DEPTH: 0.73 M) IMMEDIATELY D/S, ADJACENT TO THE LEFT BANK. WOODY DEBRIS BUILD UP IS FOUND ON THE LEFT BANK NEARBY THE DOWNCUTTING SECTION. MINOR TOE EROSION IS FOUND ON THE RIGHT BANK ADJACENT TO THE CROSSING (TOE DIMENSIONS: 21.4 M LENGTH, 0.1 M UNDERCUTTING). A MAJOR SCOUR WITH DIMENSIONS (>50 M LENGTH, 1.5 M HEIGHT, 1.2 M WIDTH) IS FOUND D/S OF THE DOWNCUTTING SECTION ON THE LEFT BANK. PORTIONS OF THE SCOUR THROUGHOUT ARE BEGINNING TO RE-VEGETATE. THE MANHOLE IS 0.9 M FROM THE SCOUR ON THE NORTH SIDE AND 0.5 M FROM SCOUR ON THE SOUTH SIDE. THE SOUTH SIDE OF THE MANHOLE CHIMNEY IS EXPOSED (EXPOSED DIMENSIONS: 1 M LENGTH, 0.3 DEPTH, 0.4 M WIDTH) AND IT IS UNDERCUT BY 0.4 M. HIGH PRIORITY ASSIGNED AS THE NORTH AND SOUTH SIDE OF THE MANHOLE IS SCOURING, PUTTING THE MANHOLE AT RISK.
2018 | I-152 | Markham | Don River | German Mills Creek (DR) | 2018-07-19 | 12:37 | 12:45 | TY | JSi | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 |  |  | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 31-60 | Mixed | 12.4 | 1.53 | 8.1 | 0.49 | N | A | A | U&D | Yes | No | No | No | No | No | No | No | No | Yes | Yes | No | No | Yes |  | **POST STORM INSPECTION** THE 2018 SURVEYED DEPTH OF COVER IS 1.55 M (1.7 M AS-BUILT). FALLEN TREE IS FOUND ON THE U/S SECTION OF CROSSING CLOSER TO THE RIGHT BANK. THE TREE APPEARS TO CAUSE DOWNCUTTING WITH (DEPTH: 0.43 M) IMMEDIATELY D/S, ADJACENT TO THE LEFT BANK. WOODY DEBRIS BUILD UP IS FOUND ON THE LEFT AND RIGHT BANK NEARBY THE DOWNCUTTING SECTION. MINOR TOE EROSION IS FOUND ON THE RIGHT BANK ADJACENT TO THE CROSSING (TOE DIMENSIONS: 21.4 M LENGTH, 0.1 M UNDERCUTTING). A MAJOR SCOUR WITH DIMENSIONS (>50 M LENGTH, 1.5 M HEIGHT, 1.2 M WIDTH) IS FOUND D/S OF THE DOWNCUTTING SECTION ON THE LEFT BANK. PORTIONS OF THE SCOUR THROUGHOUT ARE BEGINNING TO RE-VEGETATE. THE SCOUR HAS EXPOSED CLAY ON THE LEFT BANK AT THE U/S LIMIT. THE MANHOLE IS 0.0 M FROM THE SCOUR ON THE NORTH SIDE AND 0.6 M FROM SCOUR ON THE SOUTH SIDE. THE NORTH SIDE OF THE MANHOLE THE CHIMNEY IS EXPOSED WITH THE BANK SLUMPING WITH DIMENSIONS (LENGTH:0.85 M, DEPTH:1.05 M, WIDTH:0.4 M). THE SOUTH SIDE OF THE MANHOLE CHIMNEY IS EXPOSED (EXPOSED DIMENSIONS: 0.6 M LENGTH, 0.75 DEPTH, 0.6 M WIDTH) AND IT IS UNDERCUT BY 0.4 M. HIGH PRIORITY ASSIGNED AS THE NORTH AND SOUTH SIDE OF THE MANHOLE IS SCOURING, PUTTING THE MANHOLE AT RISK.
2018 | I-152 | Markham | Don River | German Mills Creek (DR) | 2018-08-07 | 10:20 | 10:44 | HC | OT | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 5 |  |  |  | Active |  | No | 1.67 |  |  | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 31-60 | Mixed | 12.2 | 1.32 | 9.24 | 0.42 | N | A | A | U&D | Yes | No | No | No | No | Yes | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR & TOE EROSION & DEBRIS BUILDUP & TENSION CRACKING | **POST STORM INSPECTION** THE SANITARY MAIN (GRAVITY) CROSSES BENEATH A BED OF GRAVEL. THE 2018 SURVEYED DEPTH OF COVER IS 1.55 M (1.7 M AS-BUILT). A FALLEN TREE IS PRESENT AT THE U/S SECTION OF THE CROSSING ON THE LEFT BANK ADJACENT TO THE MANHOLE AND IS SITTING ACROSS THE CHANNEL. THERE IS MINOR DEBRIS BUILDUP BEHIND THE FAILED TREE ADJACENT TO THE MANHOLE FROM BRANCHES AND LEAF LITTER. MINOR TOE EROSION IS FOUND ON THE RIGHT BANK ADJACENT TO THE CROSSING (TOE DIMENSIONS: 21.4 M LENGTH, 0.1 M UNDERCUTTING). A MAJOR SCOUR IS PRESENT U/S OF THE CROSSING ON THE LEFT BANK (SCOUR DIMENSIONS: >50 M LENGTH, 1 M HEIGHT, 1 M WIDTH, AND 0.45 M UNDERCUTTING). THERE IS DOWNCUTTING OCCURRING ADJACENT TO THE LEFT BANK SCOUR BY 0.44 M. PORTIONS OF THE SCOUR APPEAR TO BE RE-VEGETATING THROUGHOUT. THE SCOUR HAS EXPOSED CLAY ON THE LEFT BANK AT THE U/S LIMIT. THERE HAS BEEN RECENT SLUMPING OF THE BANK THAT HAS EXPOSED THE MANHOLE CHIMNEY. THERE IS ALSO TENSION CRACKS PRESENT ADJACENT TO THE MANHOLE AT THE D/S AREA OF THE SCOUR. THE MANHOLE IS 0 M FROM THE SCOUR ON THE NORTH SIDE AND 0.6 M ON THE SOUTH SIDE. THE NORTH SIDE OF THE MANHOLE CHIMNEY IS EXPOSED (DIMENSIONS: 0.9 M LENGTH, 0.92 M DEPTH, 0.43 M WIDTH AND 0.45 M UNDERCUTTING). THE SOUTH SIDE OF THE MANHOLE CHIMNEY IS EXPOSED (DIMENSIONS: 1 M LENGTH, 0.4 M WIDTH, 0.6 M DEPTH AND 0.53 M UNDERCUTTING). HIGH PRIORITY ASSIGNED AS THE NORTH AND SOUTH SIDE OF THE MANHOLE IS SCOURING, PUTTING THE INFRASTRUCTURE AT RISK.
2018 | I-152 | Markham | Don River | German Mills Creek (DR) | 2018-08-28 | 11:03 | 11:22 | AV | OT | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 5 |  |  |  | Active |  | No | 1.67 |  |  | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 31-60 | Mixed | 11.6 | 1.39 | 8.35 | 0.37 | N | A | A | U&D | Yes | No | No | No | No | Yes | No | No | No | Yes | Yes | No | Yes | Yes | BANK SCOUR, TOE EROSION, DEBRIS BUILDUP, TENSION CRACKING & SLUMPING | **POST STORM INSPECTION** THE SANITARY MAIN (GRAVITY) CROSSES BENEATH A BED OF GRAVEL. THE 2018 SURVEYED DEPTH OF COVER IS 1.55 M (1.7 M AS-BUILT). A FALLEN TREE IS PRESENT AT THE U/S SECTION OF THE CROSSING ON THE LEFT BANK ADJACENT TO THE MANHOLE AND IS LYING ACROSS THE CHANNEL. THERE IS MINOR DEBRIS BUILDUP BEHIND THE FAILED TREE ADJACENT TO THE MANHOLE FROM BRANCHES AND LEAF LITTER. MINOR TOE EROSION IS FOUND ON THE RIGHT BANK ADJACENT TO THE CROSSING (TOE DIMENSIONS: 21.4 M LENGTH, 0.1 M UNDERCUTTING). A MAJOR SCOUR IS PRESENT U/S OF THE CROSSING ON THE LEFT BANK (SCOUR DIMENSIONS: >50 M LENGTH, 1.27 M HEIGHT, 1 M WIDTH, AND 0.45 M UNDERCUTTING). THERE IS DOWNCUTTING OCCURRING ADJACENT TO THE LEFT BANK SCOUR BY 0.61 M. PORTIONS OF THE SCOUR APPEAR TO BE RE-VEGETATING THROUGHOUT. THE SCOUR HAS EXPOSED CLAY ON THE LEFT BANK AT THE U/S LIMIT. THERE IS STILL SLUMPING AND TENSION CRACKS ADJACENT TO THE MANHOLE AT THE D/S AREA OF THE SCOUR, RESULTING IN THE EXPOSURE OF THE MANHOLE CHIMNEY. THE MANHOLE IS 0.5 M FROM THE TOP OF BANK IN THE AREA OF SLUMPING ON THE NORTH SIDE AND 0.6 M ON THE SOUTH SIDE. THE NORTH SIDE OF THE MANHOLE CHIMNEY IS EXPOSED (DIMENSIONS: 0.9 M LENGTH, 0.92 M DEPTH AND 0.5 M WIDTH). THE SOUTH SIDE OF THE MANHOLE CHIMNEY IS EXPOSED (DIMENSIONS: 1 M LENGTH, 0.4 M WIDTH, 0.7 M DEPTH AND 0.53 M UNDERCUTTING). HIGH PRIORITY ASSIGNED AS THE NORTH AND SOUTH SIDE OF THE MANHOLE IS SCOURING, PUTTING THE INFRASTRUCTURE AT RISK.
2018 | I-152 | Markham | Don River | German Mills Creek (DR) | 2018-11-05 | 12:00 | 12:15 | OT | DM | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 |  |  | No | [5 empty] | Gravel (2 - 64 mm) | Sand (< 2mm) | Live Cribwall | Rip Rap | Sand (< 2mm) | Silt | 31-60 | Grasses/Forbs | 12.4 | 1.42 | 8.73 | 0.38 | N | D | A | U&D | No | No | No | No | No | No | No | No | No | Yes | Yes | No | No | No |  | THE SANITARY MAIN (GRAVITY) CROSSES BENEATH A BED OF GRAVEL. THE 2018 SURVEYED DEPTH OF COVER IS 1.55 M (1.67 M AS-BUILT). FALLEN TREE MENTIONED IN THE PREVIOUS INSPECTION HAS BEEN REMOVED. INTERIM STRUCTURES HAVE BEEN BUILT ADJACENT TO AN EXPOSED MANHOLE CHIMNEY ON THE LEFT BANK. A CRIBWALL AND RIP RAP RETAINING WALL (DR12.02) HAS BEEN CONSTRUCTED ADJACENT TO THE MANHOLE. TWO RIP RAP REVETMENTS ARMOUR THE BANK IMMEDIATELY U/S (DR12.01) AND D/S (DR12.03) OF THE RETAINING WALL. TWO BANK SCOURS OBSERVED ALONG THE LEFT BANK. THE FIRST BANK SCOUR IS IMMEDIATELY U/S OF THE RIP RAP REVETMENT (DR12.01) (SCOUR DIMENSIONS: 18.7 M LENGTH, 1.27 M WIDTH, 1 M HEIGHT, 0.45 M UNDERCUT); AND THE SECOND BANK SCOUR IS IMMEDIATELY D/S OF THE RIP RAP REVETMENT (DR12.03) (SCOUR DIMENSIONS: 28.9 M LENGTH, 1.3 M WIDTH, 1.4 M HEIGHT). THE LEFT BANK IS SLUMPING AT VARIOUS LOCATIONS ALONG BOTH SCOURS. CHANNEL BED IS DOWNCUTTING BY 0.61 M ADJACENT TO THE U/S LIMIT OF THE FIRST SCOUR. LEANING TREES ARE OBSERVED NEAR THE D/S LIMIT OF THE SECOND SCOUR. COIR NETTING IS SURROUNDING THE MANHOLE, HOWEVER THE TOP OF BANK IS BARE OF VEGETATION. THE MANHOLE IS 3.6 M TO THE EDGE OF THE LIVE CRIBWALL. MINOR TOE EROSION ALONG THE RIGHT BANK IN AREA OF THE CROSSING (TOE EROSION DIMENSIONS: 21.4 M LENGTH, 0.1 M UNDERCUT). PRIORITY WAS REDUCED FROM CRITICAL TO HIGH AS INTERIM BANK PROTECTION IS IN PLACE (LIFESPAN OF ~ 2 YEARS), AND THE 2018 SURVEYED DEPTH OF COVER IS 1.55 M (1.67 M AS-BUILT DEPTH OF COVER).
2019 | I-152 | Markham | Don River | German Mills Creek (DR) | 2019-05-06 | 12:29 | 12:45 | SK | SD | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 |  |  | No | [5 empty] | Gravel (2 - 64 mm) | Sand (< 2mm) | Live Cribwall | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | 31-60 | Grasses/Forbs | 11.7 | 1.25 | 9.36 | 0.7 | N | D | A | U&D | No | No | No | No | No | No | No | No | No | Yes | No | No | No | No |  | The sanitary main (gravity) crosses beneath a bed of gravel. The 2018 surveyed depth of cover is 1.55 m (1.67 m as-built). Interim structures have been built adjacent to an exposed manhole chimney on the left bank. A cribwall and rip rap retaining wall (DR12.02) has been constructed adjacent to the manhole. Two rip rap revetments armour the bank immediately u/s (DR12.01) and d/s (DR12.03) of the retaining wall. Two bank scours observed along the left bank. The first bank scour is immediately u/s of the rip rap revetment (DR12.01) (scour dimensions: 18.7 m length, 1.27 m width, 1 m height, 0.45 m undercut); and the second bank scour is immediately d/s of the rip rap revetment (DR12.03) (scour dimensions: 28.9 m length, 1.3 m width, 1.4 m height). Unlike previous inspection there was no more slumping. Channel bed is downcutting by 0.61 m adjacent to the u/s limit of the first scour. Leaning trees are observed near the d/s limit of the second scour. Coir netting is surrounding the manhole, however the top of bank is bare of vegetation. The manhole is 3.6 m to the edge of the live cribwall. Minor toe erosion along the right bank in area of the crossing (toe erosion dimensions: 21.4 m length, 0.1 m undercut). Priority was reduced from critical to high as interim bank protection is in place (lifespan of ~ 2 years), and the 2018 surveyed depth of cover is 1.55 m (1.67 m as-built depth of cover).
2019 | I-152 | Markham | Don River | German Mills Creek (DR) | 2019-08-06 | 9:30 | 9:49 | SD | SK | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 |  |  | No | [5 empty] | Gravel (2 - 64 mm) | Sand (< 2mm) | Live Cribwall | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | 61-90 | Shrubs | 12.3 | 0.8 | 15.38 | 0.28 | N | D | A | U&D | Yes | No | Yes | No | No | No | No | No | No | Yes | Yes | No | No | No |  | The sanitary main (gravity) crosses beneath a bed of gravel. The 2018 surveyed depth of cover is 1.55 m (1.67 m as-built). Interim structures have been built adjacent to a previously exposed manhole chimney on the left bank. A cribwall and rip rap retaining wall (DR12.02) has been constructed adjacent to the manhole. Two rip rap revetments armour the bank immediately u/s (DR12.01) and d/s (DR12.03) of the retaining wall. Two bank scours observed along the left bank. The first bank scour is immediately u/s of the rip rap revetment (DR12.01) (scour dimensions: 18.7 m length, 1.27 m width, 1 m height, 0.45 m undercut); and the second bank scour is immediately d/s of the rip rap revetment (DR12.03) (scour dimensions: 28.9 m length, 1.3 m width, 1.4 m height). Although these bank scours are still present, they are beginning to revegetate at the time of the inspection. The channel downcutting (0.96 m) adjacent to the u/s limit of the first scour has increased in severity. Leaning trees are observed near the d/s limit of the second scour. The manhole is 3.6 m to the edge of the live cribwall. The previously mentioned toe erosion on the right bank has completely revegetated. A fallen tree is present along the bed adjacent to the left bank of the site. Priority was reduced from critical to high as interim bank protection is in place (lifespan of ~ 2 years), and the 2018 surveyed depth of cover is 1.55 m (1.67 m as-built depth of cover).
2020 | I-152 | Markham | Don River | German Mills Creek (DR) | 2020-05-26 | 10:07 | 10:29 | CM | NPa | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 |  |  | No | [5 empty] | Gravel (2 - 64 mm) | Sand (< 2mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Densely Vegetated | 61-90 | Shrubs | 13 | 1.47 | 8.84 | 0.24 | N | D | U | U&D | Yes | No | Yes | No | No | No | No | No | No | Yes | Yes | No | No | No |  | The sanitary main (gravity) crosses the channel with 1.55 m of remaining depth of cover as surveyed in 2018. Interim erosion control structures have been built on the left bank adjacent to a sanitary manhole. A live cribwall and rip rap retaining wall has been constructed adjacent to the manhole and the manhole remains 3.6 m from the top of the cribwall. Rip rap revetments protect the bank immediately u/s and d/s of the retaining wall. A bank scour (16.6 m length, 2 m width, 1.44 m height, 0.5 m undercut) is located immediately u/s from the rip rap revetment with signs of slumping. A bank scour (34 m length, 2 m width, 1.6 m height, 0.65 m undercut) is also located immediately d/s of the rip rap revetment with signs of recent slumping. A gully which measues 2.7 m long, 0.2 m wide and 0.15 m deep is present on the left bank, d/s from the crossing. Minor toe erosion is occurring on the right bank in the location of the crossing. The channel is downcutting by 0.51 m adjacent to the revetment and 0.67 m adjacent to the u/s limit of the bank scour. A fallen tree is still present along the bed, adjacent to the left bank. Leaning trees are observed at the mid-section of the d/s scour
2020 | I-152 | Markham | Don River | German Mills Creek (DR) | 2020-08-28 | 9:22 | 9:35 | CM | NPa | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 |  |  | No | [5 empty] | Gravel (2 - 64 mm) | Sand (< 2mm) | Rip Rap | Sand (< 2mm) | Rip Rap | Densely Vegetated | 31-60 | Shrubs | 14.3 | 1.47 | 9.73 | 0.24 | N | D | U | U&D | Yes | No | Yes | No | No | No | No | Yes | No | Yes | Yes | No | No | No |  | Minimal changes have occurred since the previous 2020 inspection record. The most apparent change is vegetation growth throughout the adjacent structure and scours. The sanitary main (gravity) crosses the channel with 1.55 m of remaining depth of cover as surveyed in 2018. Interim erosion control structures have been built on the left bank adjacent to a sanitary manhole. A live cribwall and rip rap retaining wall has been constructed adjacent to the manhole and the manhole remains 3.6 m from the top of the cribwall. Rip rap revetments protect the bank immediately u/s and d/s of the retaining wall. A bank scour (16.6 m length, 2 m width, 1.44 m height, 0.5 m undercut) is located immediately u/s from the rip rap revetment with signs of slumping. A bank scour (34 m length, 2 m width, 1.6 m height, 0.65 m undercut) is also located immediately d/s of the rip rap revetment with signs of recent slumping. A gully which measues 2.7 m long, 0.2 m wide and 0.15 m deep is present on the left bank, d/s from the crossing. Minor toe erosion is occurring on the right bank in the location of the crossing. The channel is downcutting by 0.51 m adjacent to the revetment and 0.67 m adjacent to the u/s limit of the bank scour. A fallen tree is still present along the bed, adjacent to the left bank. Leaning trees are observed at the mid-section of the d/s scour.
2021 | I-152 | Markham | Don River | German Mills Creek (DR) | 2021-07-14 | 10:00 | 10:30 | NPa | SV | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 | 1.55 | 2018-07-18 | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Live Cribwall | Densely Vegetated | Sand (< 2mm) | 91-100 | Grasses/Forbs | 12.5 | 1.4 | 8.93 | 0.22 | N | D | U&D | A | Yes | No | No | No | No | No | No | Yes | No | Yes | No | No | No | No |  | Minimal changes have occurred at this site since the previous 2020 inspection record; scours noted u/s and d/s of the crossing on the left bank are revegetating. The sanitary main (gravity) crosses a straight section of the watercourse with 1.55 m of remaining depth of cover as surveyed in 2018. A rip rap revetment and live cribwall (DR12.02) has been built adjacent to the manhole on the left bank. The bank scour previously noted u/s of the crossing on the left bank now measures 7.4 m in length, 2.0 m in width, 1.44 m in height with a 0.50 m undercut along the crest; the d/s portion of the scour has revegetated. The bank scour d/s of the crossing measuring 34 m in length, 2.0 m in width, and 1.6 m in height with an undercut if 0.15 m along the crest is still evident with signs of recent slumping (large clumps of vegetated soil are present at the toe). Minor toe erosion is occurring on the right bank in the area of the crossing. The channel bed is downcutting in two areas; the first downcut measures 0.3 m and is located in front of the erosion control structure and the second downcut u/s of the erosion control structure measures 0.9. There is still a gully evident d/s of the area of the crossing that measures 2.7 m in length (crosses informal path), 0.3 m in width and 0.2 m in depth. A fallen tree is still present along the bed, adjacent to the left bank. There is minor debris buildup along the toe of the u/s scour and leaning trees are observed at the midsection of the d/s scour.
2022 | I-152 | Markham | Don River | German Mills Creek (DR) | 2022-06-14 | 9:00 | 9:20 | AP | LS | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 4 |  |  |  | Active |  | No | 1.67 | 1.55 | 2018-07-18 | No | [5 empty] | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Live Cribwall | Densely Vegetated | Sand (< 2mm) | 61-90 | Grasses/Forbs | 10.84 | 0.22 | 49.27 | 0.22 | N | D | U&D | A | Yes | No | No | No | No | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Toe erosion, displacement and undermined trees | Moderate changes have occurred at the site since the previous inspection. The sanitary main (gravity) crosses a straight section of the watercourse with 1.55 m of remaining depth of cover as surveyed in 2018. A rip rap revetment and live cribwall (DR12.02) has been built adjacent to the manhole on the left bank. Displacement of the rip rap revetment is taking place. The bank scour previously noted u/s of the crossing on the left bank now measures 7.4 m in length, 0.9 m in width (a 1.1 m decrease), 1.30 m in height (a 0.14 m decrease) with a 0.40 m undercut (a 0.10 m decrease) along the crest (a 0.10 m decrease); the d/s portion of the scour has revegetated. The bank scour d/s of the crossing now measures 34 m in length, 2.0 m in width, and 1.35 m in height (a 0.25 m decrease) with an undercut if 0.30 m (a 0.15 m increase) along the crest is still evident with signs of recent slumping. Minor toe erosion is occurring on the right bank in the area of the crossing. A sediment/stone bar is present along the right bank throughout the crossing and is now diverting flow towards the right bank. The channel bed is downcutting in three areas; the first downcut measures 0.60 m (a 0.30 m increase) and is located in front of the erosion control structure while the second downcut u/s of the erosion control structure measuring 0.9 m and the final downcut (new) is found immediately d/s of the sediment/stone bar measuring 0.47 m. There is still a gully evident d/s of the area of the crossing that measures 2.7 m in length (crosses informal path), 0.40 m in width (a 0.10 m increase) and 1.7 m in depth (a 1.5 m increase). A fallen tree is still present along the bed, adjacent to the left bank. There is minor debris buildup along the toe of the u/s scour and leaning trees are observed at the midsection of the d/s scour. Two undermined trees are now present along the left bank at the u/s limit of the site measuring 0.75 m and at the d/s limit measuring 0.40 m.
2023 | I-152 | Markham | Don River | German Mills Creek (DR) | 2023-07-06 | 10:21 | 10:41 | ALo | KLa | Intersection | Sanitary Main (Gravity) | MHLC180 - MHLC181 | 630811.85 | 4852616.47 | LESLIE STREET | STEELES AVENUE WEST | PARK ON GERMAN MILLS ROAD ADJACENT TO FORMAL FOOTPATH. TAKE PATH DOWN SLOPE AND SOUTH TO SITE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with P-060. | 1 |  |  |  | Active |  | No | 1.67 | 1.55 | 2018-07-18 | No | [5 empty] | Cobbles (64 - 256 mm) | Gravel (2 - 64 mm) | Cobbles (64 - 256 mm) | Silt | Cobbles (64 - 256 mm) | Densely Vegetated | 0-30 | Grasses/Forbs | 10.5 | 1.5 | 7 | 0.2 | N | U&D | U&D | A | Yes | No | No | No | No | No | No | No | No | No | Yes | No | No | Yes | Displacement | Major changes have occurred to site inspections since previous inspection due to restoration works on site. The sanitary main (gravity) crosses a straight section of the watercourse. Downcutting adjacent to the left bank at the u/s limit measures 0.60 m. Scour u/s of crossing on left bank is no longer present. Exposed coir netting along toe of right bank can be found u/s of crossing. Scour has been covered by revetment and covered by coir netting. Two leaning trees can be found on the left bank at the u/s limit of the site. The channel bed is well protected by rip rap in the area of the crossing. The right bank in the area of the crossing is protected by cobbles. Cobble revetment adjacent to the manhole on the left bank is experiencing minor displacement and sediment buildup at d/s limit of revetment. The other scour located d/s of the crossing on the left bank is no longer present. Directly d/s of the revetment there is a sediment bar on the left bank. D/S of the crossing root wads are present protecting the right bank. Coir netting is also present along the right bank. Downcutting is also present d/s of crossing adjacent to root wads measures 0.85 m at max depth.
2011 | P-060 | Markham | Don River | German Mills Creek (DR) | 2011-08-12 | 10:22 | 10:52 | MJ | SL | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually | DC | Active |  | Yes | 2.9 |  |  | No | 3.4 | -1 |  |  | 70 | Gravel (2 - 64 mm) | Sand (< 2mm) | Sand (< 2mm) | N/A | Sand (< 2mm) | N/A | 31-60 | Grasses/Forbs | 11.7 | 2.25 | 5.2 | 1.23 | N | A | A | U&D | Yes | No | No | No | No | No | No | No | No | Yes | Yes | No | Yes | No |  | DUE TO SIGNIFICANT LATERAL MIGRATION ALONG THE LEFT BANK, THE SANITARY MAIN NOW APPEARS TO CROSS UNDER THE CHANNEL BED. THE LEFT BANK IS ERODING AT HIGH FLOW, CREATING A MAJOR EROSION SCAR ALONG THE ENTIRE LENGTH OF THE OUTSIDE MEANDER. THERE APPEARS TO BE DOWNCUTTING ALONG THE CHANNEL BED NEAR THE LEFT BANK. HIGH PRIORITY AS THE INFRASTRUCTURE MAY BE LOCATION BENEATH THE CHANNEL BED AND DEPTH OF COVER IS NOT KNOWN. CURRENT ALIGNMENT OF WATERCOURSE IS DIFFERENT THAN AS-BUILT DUE TO DEVELOPMENT OF AREA - THEREFORE AS-BUILT DISTANCE IS LIKELY NOT APPLICABLE. |  |  |  | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2013 | P-060 | Markham | Don River | German Mills Creek (DR) | 2013-06-17 | 11:15 | 0:11 | SL | CP | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually | SL | Active |  | Yes | 2.9 |  |  | No | 3.4 | -3.3 |  |  |  | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | N/A | Sheet Piling | N/A | 91-100 | Grasses/Forbs | 12.3 | 2.05 | 6 | 0.99 | N | A | A | U&D | Yes | No | Yes | No | Yes | No | No | No | No | Yes | Yes | No | Yes | No |  | THE WATERCOURSE HAS MIGRATED OVER A SECTION OF THE SANITARY MAIN. THE SURVEYED DEPTH OF COVER IS 0.7 M OVER THE ENCROACHED MAIN, 3.3 M FROM THE ADJACENT BANK. DEEP POOL IN AREA OF ENCROACHMENT, LIKELY SUSCEPTIBLE TO EDDYING, EROSION AND DOWNCUTTING AT HIGH FLOW. RECENT BANK SLUMPING IS OBSERVED ADJACENT TO PIN 1. HIGH PRIORITY ASSIGNED AS THE WATERCOURSE HAS MOVED OVER THE INFRASTRUCTURE AND THE DEPTH OF COVER IS ONLY 0.7 M OVER THE ENCROACHED MAIN. | 1.95 | 4.4 | 1.5 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2014 | P-060 | Markham | Don River | German Mills Creek (DR) | 2014-06-17 | 10:41 | 11:06 | JS | OT | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually | SL | Active |  | No | 2.9 | 0.92 |  | No | 3.4 | -3.4 | Surveyed | 2014-05-23 |  | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Gravel (2 - 64 mm) | 91-100 | Trees | 14.1 | 1.98 | 7.12 | 0.62 | N | A | A | U&D | Yes | No | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No | Yes | BANK SCOUR | THE WATERCOURSE HAS MIGRATED OVER A SECTION OF THE SANITARY MAIN. THE 2014 SURVEYED DEPTH OF COVER IS 0.9 M. THE ENCROACHED MAIN IS LOCATED WITHIN THE WATERCOURSE 3.4 M FROM THE ADJACENT BANK. SIGNS OF MINOR DOWNCUTTING IN AREA OF ENCROACHMENT AT TIME OF INSPECTION. BOTH BANKS ARE EXPERIENCING SCOURING (>25 M), WHICH EXTEND D/S BEYOND THE PROXIMITY SITE. THE LEFT BANK IS BEING UNDERCUT BY 1.1 M. MAJOR DEBRIS JAM PRESENT D/S OF PROXIMITY SITE. HIGH PRIORITY ASSIGNED AS THE WATERCOURSE HAS MOVED OVER THE INFRASTRUCTURE AND THE DEPTH OF COVER IS ONLY 0.9 M OVER THE ENCROACHED MAIN. | 1.4 | 4.4 | 1.4 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2014 | P-060 | Markham | Don River | German Mills Creek (DR) | 2014-08-12 | 11:48 | 0:26 | JS | OT | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually | SL | Active |  | Yes | 2.9 |  |  | No | 3.4 | -3.4 | Estimated |  | 70 | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Gravel (2 - 64 mm) | 91-100 | Trees |  |  |  | 0.91 | N | A | A | U&D | Yes | No | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No | Yes | BANK SCOUR | Site reinspected following storm events late July to early August 2014. Recession of 0.7 m along the left bank scour at Pin 1 (just downstream of manhole LC-09). The scour in area of Pin 1 and manhole is significantly undercut with signs of recent movement. Scouring and undercutting of the bank near the manhole since the last inspection has undermined a tree, causing it to lean into the channel. The caving bank near the leaning tree has pulled the land away from the side of the manhole, creating a 0.3 m void along the chimney wall. The manhole is currently located 0.8 m from the bank (decrease of 1.5 m since May 23, 2014 at time of last site survey). No major changes in monitoring stations Pin 2 and Pin 3. The 2014 surveyed depth of cover over the encroached sanitary main is 0.9 m. The sanitary main is located 3.4 m from the top of the scour at the widest point. Priority remains high due to the risk to the encroached main with a shallow depth of cover and the risk to the manhole. (Note: Manhole found east of MH09 is just a discarded frame and cover.) | 0.7 | 4.4 | 1.4 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2015 | P-060 | Markham | Don River | German Mills Creek (DR) | 2015-05-20 | 9:17 | 10:17 | OT | DM | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually | SL | Active |  | No | 2.9 | 0.67 |  | No | 3.4 | -3.32 | Surveyed | 2015-10-19 | 70 | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Gravel (2 - 64 mm) | 91-100 | Mixed | 13.1 | 1.86 | 7.04 | 0.68 | N | A | A | U | Yes | No | Yes | No | No | No | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR | THE WATERCOURSE HAS MIGRATED OVER THE SANITARY MAIN. THE 2015 SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.7 M. BANK SLUMPING AND SETTLEMENT AT THE BASE OF THE NORTH SANITARY MANHOLE (MH09) HAS EXPOSED A PORTION OF THE UPPER CHIMNEY. THE MANHOLE IS LOCATED 0.5 M FROM THE LEFT BANK AT THE CLOSEST POINT AND IS AT RISK OF BEING COMPLETELY OUTFLANKED. THE LEFT BANK HAS ALMOST RECEDED TO THE SANITARY SEWER U/S OF THE CURRENT AREA OF ENCROACHMENT (NEAR PIN 1). HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED BELOW THE WATERCOURSE AND THE DEPTH OF COVER OVER THE ENCROACHED MAIN IS ONLY 0.7 M; THE SANITARY MANHOLE AT THE U/S SECTION OF THE PROXIMITY SITE IS ALSO AT RISK DUE TO BANK EROSION AND INSTABILITY. | 1.4 | 4.4 | 1.4 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2017 | P-060 | Markham | Don River | German Mills Creek (DR) | 2017-06-28 | 11:48 | 12:10 | OT | RC | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually | JSP | Active |  | No | 2.9 |  |  | No | 3.4 | -3.3 | Estimated |  | 70 | [31 empty] | **POST STORM INSPECTION: MINOR SLUMPING OBSERVED THROUGHOUT SCOUR ADJACENT TO SITE. NO MAJOR DEFICIENCIES OBSERVED SINCE LAST INSPECTION. SEE PREVIOUS INSPECTION FOR COMMENTS. | 1.4 | 4.4 | 1.4 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595 | bar: Yes to Yes
2018 | P-060 | Markham | Don River | German Mills Creek (DR) | 2018-04-06 | 11:00 | 11:40 | OT | RC | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 |  |  | No | 3.4 | -3.3 | Estimated |  | 69 | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 31-60 | Mixed | 13.8 | 2.1 | 6.57 | 0.8 | N | A | A | U&D | Yes | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | BANK SCOUR, EXPOSED MANHOLE CHIMNEY | THE WATERCOURSE HAS MIGRATED OVER THE SANITARY SEWER AND A MANHOLE IS AT RISK U/S OF THE ENCROACHMENT. THE DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.7 M (AS SURVEYED IN 2015). MINOR TOE EROSION ADJACENT TO PIN 1. THE BANK IS SCOURING THROUGHOUT ENTIRE PROXIMITY SITE (SCOUR DIMENSIONS: >50 M LENGTH, 1.25 M WIDTH, 1.4 M HEIGHT) AND A MAXIMUM UNDERCUT BY 0.6 M. CHANNEL BED IS DOWNCUTTING ADJACENT TO PIN 3 IN AREA OF ENCROACHMENT BY 1.25 M. BANK SLUMPING AROUND A SANITARY MANHOLE HAS EXPOSED A PORTION OF ITS UPPER CHIMNEY. THE MANHOLE IS LOCATED 0.5 M FROM THE SCOUR AT THE CLOSEST POINT; MANHOLE IS AT RISK OF BEING COMPLETELY OUTFLANKED. MAJOR DEBRIS BUILDUP D/S OF PROXIMITY SITE. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED BELOW THE WATERCOURSE AND A SANITARY MANHOLE IS AT RISK. | 1.4 | 4.2 | 1.4 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2018 | P-060 | Markham | Don River | German Mills Creek (DR) | 2018-04-18 | 10:50 | 11:00 | OT | DG | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 |  |  | No | 3.4 | -3.3 | Estimated |  | 67 | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 0-30 | Grasses/Forbs |  |  |  |  | N | A | A | U&D | Yes | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | BANK SCOUR | POST STORM INSPECTION, NO CHANGES SINCE PREVIOUS INSPECTION. THE WATERCOURSE HAS MIGRATED OVER THE SANITARY MAIN AND A MANHOLE IS AT RISK U/S OF THE ENCROACHMENT. THE 2015 SURVEYED DEPTH OF COVER OVER THE ENCROACHMENT IS 0.7 M. THE BANK IS SCOURING THROUGHOUT ENTIRE PROXIMITY SITE (SCOUR DIMENSIONS: >50 M LENGTH, 1.25 M WIDTH, 1.4 M HEIGHT). CHANNEL IS DOWNCUTTING ADJACENT TO PIN 3, IN AREA OF ENCROACHMENT. MINOR DEBRIS BUILDUP IMMEDIATELY U/S OF THE PINBANK IS SLUMPING ON THE SOUTH SIDE OF A SANITARY MANHOLE, EXPOSING A PORTION OF THE CHIMNEY. THE MANHOLE IS LOCATED 0.5 M FROM THE SCOUR AT THE CLOSEST POINT; MANHOLE IS AT RISK OF BEING COMPLETELY OUTFLANKED. MAJOR DEBRIS BUILDUP D/S OF PROXIMITY SITE. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED BELOW THE WATERCOURSE AND A SANITARY MANHOLE IS AT RISK. | 1.4 | 4.2 | 1.4 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2018 | P-060 | Markham | Don River | German Mills Creek (DR) | 2018-07-10 | 11:38 | 12:05 | HC | OT | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 |  |  | No | 3.4 | -2.92 | Surveyed | 2018-07-18 | 67 | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 31-60 | Mixed | 9.5 | 1.45 | 6.55 | 0.72 | N | A | A | U&D | Yes | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | BANK SCOUR & EXPOSED CHIMNEY | THE WATERCOURSE HAS MIGRATED OVER THE SANITARY SEWER AND A MANHOLE IS AT RISK U/S OF THE ENCROACHMENT. THE DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.63 M (AS SURVEYED IN 2018). MINOR TOE EROSION IS FOUND ADJACENT TO PIN 1. THE BANK IS SCOURING THROUGHOUT ENTIRE PROXIMITY SITE (SCOUR DIMENSIONS: >50 M LENGTH, 1.1 M WIDTH, 1.45 M HEIGHT) AND A MAXIMUM UNDERCUT BY 0.5 M. CHANNEL BED IS DOWNCUTTING ADJACENT TO PIN 3 IN AREA OF ENCROACHMENT BY 1.10 M. BANK SLUMPING AROUND A SANITARY MANHOLE HAS EXPOSED A PORTION OF ITS UPPER CHIMNEY. LEANING TREE PRESENT TO THE ADJACENT TO PIN 3. THE MANHOLE IS LOCATED 0.5 M FROM THE SCOUR AT THE CLOSEST POINT; MANHOLE IS AT RISK OF BEING COMPLETELY OUTFLANKED. MAJOR WOODY DEBRIS BUILDUP D/S OF PROXIMITY SITE. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED BELOW THE WATERCOURSE AND A SANITARY MANHOLE IS AT RISK. | 1.4 | 4.2 | 1.4 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2018 | P-060 | Markham | Don River | German Mills Creek (DR) | 2018-07-19 | 12:15 | 12:30 | JSi | OT | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 |  |  | No | 3.4 | -2.92 | Estimated |  | 67 |  |  | Sand (< 2mm) | Silt | Gravel (2 - 64 mm) | Silt | 31-60 | Mixed | 8.6 | 1.05 | 8.19 | 0.4 | N | A | A | U&D | Yes | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | BANK SCOUR, EXPOSED CHIMNEY | THE WATERCOURSE HAS MIGRATED OVER THE SANITARY SEWER AND A MANHOLE IS AT RISK U/S OF THE ENCROACHMENT. THE DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.63 M (AS SURVEYED IN 2018). MINOR TOE EROSION IS FOUND ADJACENT TO PIN 1. THE BANK IS SCOURING THROUGHOUT ENTIRE PROXIMITY SITE (SCOUR DIMENSIONS: >50 M LENGTH, 1.1 M WIDTH, 1.45 M HEIGHT) AND A MAXIMUM UNDERCUT BY 0.5 M. CHANNEL BED IS DOWNCUTTING ADJACENT TO PIN 3 IN AREA OF ENCROACHMENT BY 1.10 M. BANK SLUMPING AROUND A SANITARY MANHOLE HAS EXPOSED A PORTION OF ITS UPPER CHIMNEY. LEANING TREE PRESENT TO THE ADJACENT TO PIN 3. THE MANHOLE IS LOCATED 0.5 M FROM THE SCOUR AT THE CLOSEST POINT. MAJOR WOODY DEBRIS BUILDUP D/S OF PROXIMITY SITE. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS EXPOSED BELOW THE WATERCOURSE AND THE SANITARY MANHOLE IS AT RISK. | 1.4 | 4.2 | 1.4 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2018 | P-060 | Markham | Don River | German Mills Creek (DR) | 2018-08-07 | 10:47 | 10:58 | HC | OT | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 |  |  | No | 3.4 | -2.92 | Estimated |  | 67 | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 31-60 | Grasses/Forbs | 9.6 | 0.93 | 10.32 | 0.33 | D | A | U&D | A | Yes | No | No | No | No | No | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR & DEBRIS BUILDUP | THE WATERCOURSE HAS MIGRATED OVER THE SANITARY SEWER AND A MANHOLE IS AT RISK U/S OF THE ENCROACHMENT. THE DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.63 M (AS SURVEYED IN 2018). MINOR TOE EROSION IS FOUND ADJACENT TO PIN 1. THE BANK IS SCOURING THROUGHOUT THE ENTIRE PROXIMITY SITE (SCOUR DIMENSIONS: >50 M LENGTH, 1.05 M WIDTH, 1.05 M HEIGHT, AND 0.45 M UNDERCUTTING). THE CHANNEL BED IS DOWNCUTTING BY 0.53 M ADJACENT TO THE SCOUR IN AREA OF PROXIMITY. BANK SLUMPING AROUND A SANITARY MANHOLE HAS EXPOSED A PORTION OF ITS UPPER CHIMNEY. A LEANING TREE IS PRESENT ADJACENT TO PIN 3. THE MANHOLE IS LOCATED 0.5 M FROM THE SCOUR AT THE CLOSEST POINT. MINOR DEBRIS BUILDUP ADJACENT TO PIN 3. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS EXPOSED BELOW THE WATERCOURSE AND THE INFRASTRUCTURE IS AT RISK. | 1.4 | 4 | 1.2 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2018 | P-060 | Markham | Don River | German Mills Creek (DR) | 2018-08-28 | 11:28 | 11:44 | AV | OT | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 | 0.63 | 2018-07-18 | No | 3.4 | -2.92 | Surveyed | 2018-07-18 | 67 | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 31-60 | Grasses/Forbs | 8.5 | 1.43 | 5.94 | 0.65 | D | A | U&D | A | Yes | No | No | No | No | No | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR, SLUMPING & TOE EROSION | THE WATERCOURSE HAS MIGRATED OVER THE SANITARY SEWER AND A MANHOLE IS AT RISK U/S OF THE ENCROACHMENT. THE DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.63 M (AS SURVEYED IN 2018). MINOR TOE EROSION IS FOUND ADJACENT TO PIN 1. THE LEFT BANK IS SCOURING THROUGHOUT THE ENTIRE PROXIMITY SITE (SCOUR DIMENSIONS: >50 M LENGTH, 1.05 M WIDTH, 1.35 M HEIGHT, AND 0.6 M UNDERCUTTING). THE CHANNEL BED IS DOWNCUT BY 0.53 M ADJACENT TO THE SCOUR IN AREA OF PROXIMITY. BANK SLUMPING AROUND A SANITARY MANHOLE HAS EXPOSED A PORTION OF ITS UPPER CHIMNEY. THE MANHOLE IS 0.5 M FROM THE TOP OF BANK IN THE AREA OF SLUMPING ON THE NORTH SIDE AND 0.6 M ON THE SOUTH SIDE. THE NORTH SIDE OF THE MANHOLE CHIMNEY IS EXPOSED (DIMENSIONS: 0.9 M LENGTH, 0.92 M DEPTH AND 0.5 M WIDTH). THE SOUTH SIDE OF THE MANHOLE CHIMNEY IS EXPOSED (DIMENSIONS: 1 M LENGTH, 0.4 M WIDTH, 0.7 M DEPTH AND 0.53 M UNDERCUTTING). A LEANING TREE IS PRESENT ADJACENT TO PIN 2. THE MINOR DEBRIS BUILDUP ADJACENT TO PIN 3 NOTED IN THE PREVIOUS INSPECTION IS NO LONGER PRESENT. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS EXPOSED BELOW THE WATERCOURSE AND THE INFRASTRUCTURE IS AT RISK. | 1.4 | 4 | 1.2 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2019 | P-060 | Markham | Don River | German Mills Creek (DR) | 2019-05-28 | 11:22 | 0:10 | SK | SD | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 |  |  | No | 3.4 |  |  |  | 62 | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 91-100 | Mixed | 10.4 | 1.35 | 7.7 | 0.3 | D | A | U&D | A | Yes | Yes | No | No | Yes | No | No | No | No | Yes | Yes | No | No | Yes | Toe erosion | The watercourse has migrated over the sanitary sewer and a manhole is at risk u/s of the encroachment. The depth of cover over the encroached main is 0.63 m (as surveyed in 2018). Minor toe erosion is found adjacent to pin 1. There is also eddying along the l/b near pin 1. The left bank is scouring throughout the entire proximity site (scour dimensions: >50 m length, 1.05 m width, 1.35 m height, and 0.6 m undercutting). The channel bed is downcutting by 0.85 m adjacent to the scour in area of proximity. The chimney of the manhole is no longer exposed as there is coir netting around it to protect the manhole. A leaning tree is present adjacent to pin 2. The minor debris buildup adjacent to pin 3 noted in the previous inspection is no longer present. High priority assigned as the sanitary main is exposed below the watercourse and the infrastructure is at risk at the time of inspection. | 1.4 | 4 | 1.2 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2021 | P-060 | Markham | Don River | German Mills Creek (DR) | 2021-07-14 | 11:10 | 11:40 | NPa | SV | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 | 0.63 | 2018-07-16 | No | 3.4 | -2.92 | Surveyed | 2018-07-16 |  | Gravel (2 - 64 mm) | Sand (< 2mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 61-90 | Mixed | 11 | 2 | 5.5 | 0.3 | N | U&D | A | U&D | Yes | No | No | No | Yes | No | No | No | No | Yes | No | No | No | No |  | No changes were observed to bank conditions or pin measurements from the previous inspection. The sanitary main (gravity) is located on the left bank of the watercourse, however, the watercourse has migrated over the sanitary main by 2.92 m with 0.63 m remaining depth of cover as surveyed in 2018. A large scour extends through the entire proximity site measuring > 50 m in length, 1.3 m in width and 1.2 m in height. The scour is being undercut along the toe adjacent to Pin 1 to a max depth of 0.55 m. There are multiple leaning trees and exposed roots within this scour. Eddying is occurring u/s of Pin 1 adjacent to the location of a gully which measures 2.7 m in length (crosses informal path), 0.3 m in width and 0.2 m in depth. The channel bed is downcutting by 0.65 m adjacent to Pin 1, however, downcutting was not observed in the area of encroachment at the time of inspection. Minor toe erosion is occurring adjacent to Pin 2. |  |  |  | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2022 | P-060 | Markham | Don River | German Mills Creek (DR) | 2022-06-14 | 11:30 | 12:00 | AP | LS | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 | 0.63 | 2018-07-16 | No | 3.4 | -2.92 | Surveyed | 2018-07-16 |  | Gravel (2 - 64 mm) | Sand (< 2mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 61-90 | Mixed | 13.06 | 0.83 | 15.73 | 0.71 | N | U&D | A | U&D | Yes | No | No | No | Yes | No | No | Yes | No | Yes | Yes | No | No | Yes | Toe erosion and exposed roots | Minor changed occurred at the site since the previous inspection. The sanitary main (gravity) is located on the left bank of the watercourse, however, the watercourse has migrated over the sanitary main by 2.92 m with 0.63 m remaining depth of cover as surveyed in 2018. No changes in the pin measurements have occurred. A large scour extends through the entire proximity site measuring > 50 m in length, 1.3 m in width, 1.5 m in height (a 0.30 m increase). The scour is being undercut along the toe adjacent to Pin 1 to a max depth of 0.60 m (a 0.05 m increase). There are multiple leaning trees and exposed roots throughout the scour. Eddying is occurring u/s of Pin 1 adjacent to the location of a gully which measures 2.7 m in length (crosses informal path), 0.40 m in width (a 0.10 m increase) and 1.7 m in depth (a 1.5 m increase). Stone bars are present along the right bank of the site as well at the d/s limit. The channel bed is downcutting by 0.70 m (a 0.05 m increase) adjacent to Pin 1. Minor toe erosion is occurring adjacent to Pin 2. Some woody debris is accumulating along both banks. |  |  |  | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2023 | P-060 | Markham | Don River | German Mills Creek (DR) | 2023-07-06 | 11:04 | 11:23 | KLa | ALo | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 1 |  | Annually |  | Active |  | No | 2.9 | 0.63 | 2018-07-16 | No | 3.4 | -2.92 | Surveyed | 2018-07-16 |  | Cobbles (64 - 256 mm) | Sand (< 2mm) | Cobbles (64 - 256 mm) | Silt | Cobbles (64 - 256 mm) | Silt | 0-30 | N/A | 15.4 | 1.34 | 11.49 | 0.21 | N | U | U&D | A | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No |  | Major changes have occurred at the site since the pervious inspections; restoration works have been done in the area. The sanitary main (gravity) is located on the left bank of the watercourse, and the watercourse is no longer migrated over the sanitary main. Due to restoration work in the site area pin 4 (manhole) and pin 5 were added as new pins. The scour in the pervious inspection no longer observed as coir netting is present throughout the left bank and is re-vegetating. The left bank is protected by a cobble stone revetment throughout the entire site and cobble stone also protects the channel bed at the midsection of the site. The area of toe erosion is no longer evident and the bank is protected by the cobble stone revetment and cedar sweepers. Downcutting of 0.44 m is present in an area of pooling at the d/s limit and downcutting of 0.46 m is present in an area of pooling at the u/s limit. A sediment bar is present at the u/s limit of the site and sediment buildup is occurring along the u/s limit of the revetment. |  |  |  | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2020 | P-060 | Markham | Don River | German Mills Creek (DR) | 2020-08-28 | 9:39 | 10:05 | CM | NPa | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 | 0.63 | 2018-07-16 | No | 3.4 | -2.92 | Surveyed | 2018-07-16 | 63 | Gravel (2 - 64 mm) | Sand (< 2mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 31-60 | Mixed | 12.4 | 2.2 | 5.64 | 0.55 | N | A | A | A | Yes | No | No | No | Yes | No | No | Yes | No | Yes | Yes | No | No | No |  | No significant changes were observed and bank recession was observed adjacent to the monitoring pins since the previous 2020 inspection. The watercourse has migrated over the sanitary by 2.92 m with 0.63m of remaining depth of cover over the encroached sanitary main as surveyed in 2018. No movement was observed adjacent to the monitoring pins since the previous inspection. A large scour (>50 m length, ~1.3 m width, ~1.2 m height) is located throughout the entire left bank with several exposed tree roots and leaning trees. Eddying is occurring adjacent to Pin 1 is an eddy and the toe of the bank is undercut by 0.6 m. A gully (2.3 m length, 0.4 m width, 0.2 m depth) is present along the tableland, u/s of pin 1. Channel downcutting of 0.6 m Is occurring adjacent to pin 1 and downcutting of 0.45 m is present in the area of encroachment. Leaning trees and minor accumulation of debris are occurring throughout the entire site. |  |  |  | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2012 | P-060 | Markham | Don River | German Mills Creek (DR) | 2012-06-26 | 11:45 | 12:08 | CR | RP | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually | DC | Active |  | Yes | 2.9 | 0.73 |  | No | 3.4 | -3.3 | Surveyed | 2012-07-17 | 71 | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | N/A | Densely Vegetated | Sand (< 2mm) | 31-60 | Grasses/Forbs | 11.2 | 1.8 | 6.22 | 1.2 | N | A | A | U&D | Yes | No | Yes | No | No | No | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR | LATERAL MIGRATION HAS CAUSED THE WATERCOURSE TO MOVE OVER A SECTION OF THE INFRASTRUCTURE. THE SANITARY MAIN IS NOW LOCATED WITHIN THE CHANNEL 3 M FROM THE LEFT BANK. THE SURVEYED DEPTH OF COVER OF 0.7 M. THE LEFT BANK IS ERODING AT HIGH FLOW WITH SIGNIFICANT UNDERCUTTING ALONG THE TOE AND DOWNCUTTING OF THE ADJACENT BED. HIGH PRIORITY ASSIGNED AS THE WATERCOURSE HAS MOVED OVER THE INFRASTRUCTURE AND THE DEPTH OF COVER IS ONLY 0.7 M OVER THE ENCROACHED SANITARY MAIN. | 2.45 | 4.6 |  | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2016 | P-060 | Markham | Don River | German Mills Creek (DR) | 2016-06-10 | 12:20 | 13:10 | KY | OT | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually | SL | Active |  | No | 2.9 |  |  | No | 3.4 | -3.3 | Estimated |  | 69 | Cobbles (64 - 256 mm) | Sand (< 2mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Gravel (2 - 64 mm) | 91-100 | Mixed | 12.8 | 2 | 6.4 | 0.82 | N | A | A | U | Yes | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | BANK SCOUR, SLUMPING, EXPOSED MANHOLE | THE WATERCOURSE HAS MIGRATED OVER THE SANITARY SEWER AND A MANHOLE IS AT RISK. THE DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.7 M (AS SURVEYED IN 2015). BANK SLUMPING AND MOVEMENT AROUND A SANITARY MANHOLE HAS EXPOSED A PORTION OF ITS UPPER CHIMNEY. THE MANHOLE IS LOCATED 0.5 M FROM THE SCOUR AT THE CLOSEST POINT; MANHOLE IS AT RISK OF BEING COMPLETELY OUTFLANKED. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED BELOW THE WATERCOURSE AND A SANITARY MANHOLE IS AT RISK. | 1.4 | 4.4 | 1.4 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2017 | P-060 | Markham | Don River | German Mills Creek (DR) | 2017-05-12 | 12:29 | 13:02 | OT | KY | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually | JSP | Active |  | No | 2.9 |  |  | No | 3.4 | -3.3 | Estimated |  | 70 | Sand (< 2mm) | Gravel (2 - 64 mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 61-90 | Grasses/Forbs | 10.55 | 2 | 5.28 | 0.65 | N | A | A | U&D | Yes | No | No | No | No | No | No | No | No | Yes | No | No | Yes | Yes | BANK SCOUR, EXPOSED MANHOLE | THE WATERCOURSE HAS MIGRATED OVER THE SANITARY SEWER AND A MANHOLE IS AT RISK. THE DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.7 M (AS SURVEYED IN 2015). MINOR TOE EROSION ADJACENT TO PIN 1. THE BANK IS SCOURING THROUGHOUT ENTIRE PROXIMITY SITE (SCOUR DIMENSIONS: >50 M LENGTH, 1.25 M WIDTH, 1.4 M HEIGHT) AND A MAXIMUM UNDERCUT BY 0.6 M. CHANNEL BED IS DOWNCUTTING ADJACENT TO PIN 3 IN AREA OF ENCROACHMENT BY 1.15 M. BANK SLUMPING AND MOVEMENT AROUND A SANITARY MANHOLE HAS EXPOSED A PORTION OF ITS UPPER CHIMNEY. THE MANHOLE IS LOCATED 0.5 M FROM THE SCOUR AT THE CLOSEST POINT; MANHOLE IS AT RISK OF BEING COMPLETELY OUTFLANKED. MAJOR DEBRIS BUILDUP D/S OF PROXIMITY SITE. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED BELOW THE WATERCOURSE AND A SANITARY MANHOLE IS AT RISK. | 1.4 | 4.4 | 1.4 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2020 | P-060 | Markham | Don River | German Mills Creek (DR) | 2020-06-15 | 8:59 | 9:34 | CM | NPa | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630811.5 | 4852590.6 | LESLIE STREET | STEELES AVENUE EAST | PARK AT THE END OF LESLIE STREET ADJACENT TO WATERLOO COURT. ACCESS SITE VIA GERMAN MILLS PARK PATH. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  | Yes | 5 | Included in the geomorphic assessment of Settlers Park completed in 2015. Combined project site with I-152. | 4 |  | Annually |  | Active |  | No | 2.9 | 0.63 | 2018-07-18 | No | 3.4 | -2.92 | Surveyed | 2018-07-18 | 64 | Gravel (2 - 64 mm) | Sand (< 2mm) | Sand (< 2mm) | Silt | Sand (< 2mm) | Silt | 91-100 | Mixed | 12.1 | 2.1 | 5.76 | 0.55 | N | A | A | A | Yes | No | No | No | Yes | No | No | Yes | No | Yes | Yes | No | No | No |  | The watercourse has migrated over the sanitary by 2.92 m with 0.63m of remaining depth of cover over the encroached sanitary main as surveyed in 2018. No movement was observed adjacent to the monitoring pins since the previous inspection. A large scour (>50 m length, ~1.3 m width, ~1.2 m height) is located throughout the entire left bank with several exposed tree roots and leaning trees. Eddying is occurring adjacent to Pin 1 is an eddy and the toe of the bank is undercut by 0.6 m. A gully (2.3 m length, 0.4 m width, 0.2 m depth) is present along the tableland, u/s of pin 1. Channel downcutting of 0.45 m Is occurring adjacent to pin 1 and downcutting of 0.4 m is present in the area of encroachment. Leaning trees and minor accumulation of debris are occurring throughout the entire site. | 1.4 | 4 | 1.2 | 630815 | 4852605 | 630814 | 4852588 | 630819 | 4852595
2011 | P-062 | Markham | Don River | German Mills Creek (DR) | 2011-08-12 | 9:22 |  | MJ | SL | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630821.5 | 4852559.2 | LESLIE STREET | STEELES AVENUE WEST | PARK AT ADVENTURE VALLEY DAY CAMP NEAR STEELES AVENUE EAST AND LESLIE STREET. ASK PERMISSION AT THE MAIN DESK BEFORE ENTERING WATERCOURSE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  |  |  |  | 4 |  | Every 2 Years | DC | Active |  | Yes |  |  |  | No | 7.2 | -3 |  |  | 57 | Gravel (2 - 64 mm) | Sand (< 2mm) | Sand (< 2mm) | Live Cribwall | Sand (< 2mm) | Gravel (2 - 64 mm) | 61-90 | Mixed | 14.3 | 1.24 | 11.53 | 0.16 | N | A | U&D | A | No | No | No | Yes | No | No | No | No | No | No | No | Yes | No | No |  | BASED ON THE GID COORDINATES THE SANITARY MAIN APPEARS TO NOW RUN BENEATH THE CHANNEL ALONG THE LEFT BANK (OUTER MEANDER). A SIDE BAR HAS FORMED IN THE WATERCOURSE WHERE THE MAIN CROSSES THROUGH THE CHANNEL PROVIDING ADDITIONAL DEPTH OF COVER. CURRENT ALIGNMENT OF WATERCOURSE IS DIFFERENT THAN THE AS-BUILT AS AREA HAS BEEN DEVELOPED. S-BUILT DISTANCE IS LIKELY NOT APPLICABLE. HIGH PRIORITY AS BANK MAY HAVE MIGRATED OVERTOP OF INFRASTRUCTURE BASED ON GID COORDINATES AND DEPTH OF COVER IS NOT KNOWN. |  |  |  | 630825 | 4852548
2012 | P-062 | Markham | Don River | German Mills Creek (DR) | 2012-06-26 | 14:00 | 14:29 | RP | CR | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630821.5 | 4852559.2 | LESLIE STREET | STEELES AVENUE WEST | PARK AT ADVENTURE VALLEY DAY CAMP NEAR STEELES AVENUE EAST AND LESLIE STREET. ASK PERMISSION AT THE MAIN DESK BEFORE ENTERING WATERCOURSE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  |  |  |  | 2 |  | Every 2 Years | DC | Active |  | Yes |  | 1.66 |  | No | 7.2 | -4.54 | Surveyed | 2012-07-24 |  | Gravel (2 - 64 mm) | Sand (< 2mm) | Live Cribwall | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | 61-90 | Mixed | 15.8 | 1.39 | 11.37 | 0.36 | N | A | U&D | A | No | No | No | Yes | No | No | No | No | No | No | No | Yes | No | No |  | THE WATERCOURSE HAS MIGRATED OVER TOP OF A SECTION OF THE INFRASTRUCTURE. THE SANITARY MAIN IS NOW LOCATION WITHIN THE CHANNEL 4.5 M FROM THE LEFT BANK. THE SURVEYED DEPTH OF COVER IS 1.7 M ABOVE INFRASTRUCTURE. A LIVE CRIBWALL IS PARTIALLY ARMOURING THE LEFT BANK. SEDIMENT IS ACCUMULATING ABOVE THE ENCROACHED SANITARY MAIN AND NO SIGNS OF DOWNCUTTING WERE OBSERVED. MODERATE SCOURING BEHIND THE LIVE CRIBWALL. THERE HAS BEEN MAJOR ADJUSTMENT OF THE WATERCOURSE SINCE THE AS-BUILT WAS PREPARED. LOW PRIORITY ASSIGNED AS NO DOWNCUTTING WAS OBSERVED ABOVE THE ENCROACHED INFRASTRUCTURE AND DEPTH OF COVER IS 1.7 M. | 1.6 |  |  | 630825 | 4852548
2014 | P-062 | Markham | Don River | German Mills Creek (DR) | 2014-06-18 | 8:46 | 9:21 | OT | JS | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630821.5 | 4852559.2 | LESLIE STREET | STEELES AVENUE WEST | PARK AT ADVENTURE VALLEY DAY CAMP NEAR STEELES AVENUE EAST AND LESLIE STREET. ASK PERMISSION AT THE MAIN DESK BEFORE ENTERING WATERCOURSE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  |  |  |  | 2 |  | Every 2 Years | SL | Active |  | No |  |  |  | No | 7.2 | -4.54 | Estimated |  |  | Sand (< 2mm) | Gravel (2 - 64 mm) | Live Cribwall | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | 61-90 | Mixed | 13.3 | 1.45 | 9.17 | 0.21 | N | A | D | A | No | No | No | Yes | No | No | No | No | No | No | Yes | Yes | No | No |  | A SECTION OF THE SANITARY MAIN IS ENCROACHED AND LOCATED BENEATH THE WATERCOURSE. THE SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 1.7 M (SURVEYED 2012). NO SIGNS OF DOWNCUTTING. SEDIMENT BAR IS LOCATED ABOVE THE ENCROACHED MAIN. THE LEFT BANK IS SCOURING U/S OF AND IMMEDIATELY BEHIND THE CRIBWALL. LOW PRIORITY ASSIGNED AS THE CURRENT DEPTH OF COVER IS 1.7 M WITH NO SIGNS OF DOWNCUTTING AT TIME OF INSPECTION. | 1.6 |  |  | 630825 | 4852548 |  |  |  |  | Scheduled
2014 | P-062 | Markham | Don River | German Mills Creek (DR) | 2014-08-12 | 11:21 | 11:43 | OT | JS | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630821.5 | 4852559.2 | LESLIE STREET | STEELES AVENUE WEST | PARK AT ADVENTURE VALLEY DAY CAMP NEAR STEELES AVENUE EAST AND LESLIE STREET. ASK PERMISSION AT THE MAIN DESK BEFORE ENTERING WATERCOURSE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  |  |  |  | 2 |  | Every 2 Years | SL | Active |  | No |  |  |  | No | 7.2 | -4.54 | Estimated |  | 59 | Sand (< 2mm) | Gravel (2 - 64 mm) | Live Cribwall | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | 61-90 | Mixed |  |  |  | 0.56 | N | A | A | U&D | No | No | No | Yes | No | No | No | No | No | No | Yes | Yes | No | Yes | DISPLACEMENT, BANK SCOUR | POST-STORM INSPECTION. NO MAJOR CHANGE IN SITE CONDITIONS. NO DOWNCUTTING OBSERVED IN AREA OF SANITARY MAIN ENCROACHMENT. NO FURTHER ADVANCEMENT OF BANK SCOURS ALONG THE OUTSIDE MEANDER. PRIORITY REMAINS LOW. | 1.6 |  |  | 630825 | 4852548 |  |  |  |  | Scheduled
2016 | P-062 | Markham | Don River | German Mills Creek (DR) | 2016-06-13 | 9:17 | 9:51 | JDa | KY | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630821.5 | 4852559.2 | LESLIE STREET | STEELES AVENUE WEST | PARK AT ADVENTURE VALLEY DAY CAMP NEAR STEELES AVENUE EAST AND LESLIE STREET. ASK PERMISSION AT THE MAIN DESK BEFORE ENTERING WATERCOURSE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  |  |  |  | 2 |  | Every 2 Years | NB | Active |  | No |  | 1.66 | 2016-06-13 | No | 7.2 | -4.54 | Estimated |  | 58 | Gravel (2 - 64 mm) | Sand (< 2mm) | Live Cribwall | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | 61-90 | Mixed | 12.74 | 1.55 | 8.22 | 0.08 | N | A | U&D | A | No | No | No | Yes | No | No | No | No | No | No | Yes | No | No | Yes | MINOR SCOURING, DEBRIS ACCUMULATION | A SECTION OF THE SANITARY MAIN IS ENCROACHED AND LOCATED BENEATH THE WATERCOURSE. THE SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 1.7 M (SURVEYED 2012). NO SIGNS OF DOWNCUTTING ARE OBSERVED. SEDIMENT BAR IS LOCATED ABOVE THE ENCROACHED MAIN. THE LEFT BANK IS SCOURING U/S OF AND IMMEDIATELY BEHIND THE CRIBWALL. A MINOR DEBRIS JAM IS LOCATED U/S OF THE CROSSING DUE TO A FAILED TREE. LOW PRIORITY ASSIGNED AS THE CURRENT DEPTH OF COVER IS 1.7 M WITH NO SIGNS OF DOWNCUTTING AT TIME OF INSPECTION. | 1.6 |  |  | 630825 | 4852548 |  |  |  |  | Scheduled
2018 | P-062 | Markham | Don River | German Mills Creek (DR) | 2018-06-05 | 10:29 | 10:39 | HC | OT | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630821.5 | 4852559.2 | LESLIE STREET | STEELES AVENUE WEST | PARK AT ADVENTURE VALLEY DAY CAMP NEAR STEELES AVENUE EAST AND LESLIE STREET. ASK PERMISSION AT THE MAIN DESK BEFORE ENTERING WATERCOURSE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  |  |  |  | 2 |  | Every 2 Years |  | Active |  | No |  |  |  | No | 7.2 | -4.54 | Estimated |  | 58 | Gravel (2 - 64 mm) | Sand (< 2mm) | Live Cribwall | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | 61-90 | Mixed | 13.7 | 1.2 | 11.42 | 0.25 | N | A | U&D | A | No | No | No | No | No | No | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR & VOID | A SECTION OF THE SANITARY MAIN IS ENCROACHED AND LOCATED BENEATH THE WATERCOURSE. THE SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 1.7 M (SURVEYED 2012). NO SIGNS OF DOWNCUTTING ARE OBSERVED DURING TIME OF INSPECTION. A SEDIMENT BAR IS LOCATED ABOVE THE ENCROACHED SANITARY MAIN. THE LEFT BANK IS SCOURING U/S OF AND IMMEDIATELY BEHIND THE CRIBWALL CREATING A VOID AT 1.2 M, AND EXTENDS PAST THE LIMIT OF THE CRIBWALL (SCOUR DIMENSIONS: 17.6 M LENGTH, 1.4 M HEIGHT, 1.5 M WIDTH, 0.3 M UNDERCUTTING). A MINOR DEBRIS JAM IS LOCATED U/S OF THE CROSSING DUE TO A FAILED TREE. A MINOR DEBRIS JAM IS ALSO PRESENT AT THE D/S LIMIT OF THE CRIB WALL. VEGETATION IS GROWING THROUGH SOME SECTIONS OF THE CRIBWALL. THE RIGHT BANK HAS SEVERAL LEANING TREES THAT ARE EXPOSING TREE ROOTS. LOW PRIORITY ASSIGNED AS THE CURRENT DEPTH OF COVER IS 1.7 M WITH NO SIGNS OF DOWNCUTTING AT TIME OF INSPECTION. |  |  |  | 630825 | 4852548 |  |  |  |  | Scheduled
2021 | P-062 | Markham | Don River | German Mills Creek (DR) | 2021-07-14 | 11:40 | 12:00 | NPa | SV | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630821.5 | 4852559.2 | LESLIE STREET | STEELES AVENUE WEST | PARK AT ADVENTURE VALLEY DAY CAMP NEAR STEELES AVENUE EAST AND LESLIE STREET. ASK PERMISSION AT THE MAIN DESK BEFORE ENTERING WATERCOURSE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  |  |  |  | 2 |  | Every 2 Years |  | Active |  | No |  |  |  | No | 7.2 | -4.54 | Estimated |  |  | Gravel (2 - 64 mm) | Sand (< 2mm) | Sand (< 2mm) | Live Cribwall | Sand (< 2mm) | Silt | 61-90 | Mixed | 13.4 | 1.1 | 12.18 | 0.3 | N | A | U&D | A | No | No | No | No | No | No | No | No | No | No | No | No | No | Yes | Toe erosion, displaced timber logs | Changes have occurred to this site since the previous inspection and a new Pin 2 was added (behind the second last support post of the live cribwall). The sanitary main (gravity) is located along the left bank, however the watercourse has encroached the main by 4.54 m with a depth of cover of 1.7 m as surveyed in 2016. There are no signs of downcutting at the time of inspection and a sediment bar is present in the area of encroachment. Toe erosion is evident at along the u/s portion of the proximity site and measures 5.4 m in length. The scour previously noted behind the live cribwall is still evident and has resulted in a void of ~1.2 m. Slumping of the bank is evident u/s of the live cribwall and behind the structure. D/s of the live cribwall the scour has fully revegetated. The live cribwall appears to be in good condition with some displacement of timber logs occurring at the d/s limit of the structure. Minor woody debris is present at the toe of the cribwall. |  |  |  | 630825 | 4852548 |  |  |  |  | Scheduled
2023 | P-062 | Markham | Don River | German Mills Creek (DR) | 2023-07-06 | 11:35 | 11:55 | ALo | KLa | Proximity | Sanitary Main (Gravity) | MHLC181 - MHLC182 | 630821.5 | 4852559.2 | LESLIE STREET | STEELES AVENUE WEST | PARK AT ADVENTURE VALLEY DAY CAMP NEAR STEELES AVENUE EAST AND LESLIE STREET. ASK PERMISSION AT THE MAIN DESK BEFORE ENTERING WATERCOURSE. | City of Markham | Bottom-Land Variable | Sand Loam |  |  | WW-LC-008 | LC |  |  |  |  | 1 |  | Every 2 Years |  | Active |  | No |  |  |  | No | 7.2 | -4.54 | Estimated |  |  | Cobbles (64 - 256 mm) | Sand (< 2mm) | Cobbles (64 - 256 mm) | Sand (< 2mm) | Cobbles (64 - 256 mm) | Sand (< 2mm) | 0-30 | Grasses/Forbs | 15.9 | 1.18 | 13.47 | 0.16 | N | A | U&D | A | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No |  | Major changes have occurred to site inspections since previous inspection due to restoration works on site. The sanitary main (gravity) is located along the left bank and is no longer encroached. Pin 1 and Pin 2 have been decommissioned due to restoration works. Pin 3 was newly placed and measures 1.5 m from the crest of the bank and 11.4 m to formal footpath. Downcutting and pooling of 0.65 m can be found at the u/s limit of the site. Channel bed spanning most of the site is well protected with cobbles. A scour is present behind cobble revetment near the u/s limit of bed control is starting to revegetate with exposed coir netting and measures 10.2 m in length, 0.93 m in height and 2.15 m in width but not pose a risk to infrastructure as it has a revetment on it. Cobble revetment is protecting left bank adjacent to proximity site with cedar sweepers present. Cobble bar is starting to form adjacent to the right bank but is not impacting water flow at the time of inspection. Timber revetments present on the left bank. All revetments on site are in excellent condition. Stakings present on bank seem to be in good conditions. Downcutting of 0.50 m is occurring at the d/s limit of site. |  |  |  | 630825 | 4852548 |  |  |  |  | Post-storm Inspection
2014 | P-065 | Markham | Don River | German Mills Creek (DR) | 2014-06-18 | 9:33 | 10:06 | JS | OT | Proximity | Sanitary Main (Gravity) | MHLC182 -MHLC183 | 630838 | 4852504 | LESLIE STREET | STEELES AVENUE WEST | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, AND FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years | SL | Active |  | No |  |  |  | No | 9.1 | -0.85 | Estimated |  |  | Gravel (2 - 64 mm) | Rip Rap | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | 91-100 | Mixed | 9.7 | 1.79 | 5.42 | 0.53 | N | A | N | U | Yes | No | No | No | No | No | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR | THE TOP OF LEFT BANK IS ERODING ABOVE THE RIP RAP REVETMENT NEAR THE SANITARY MANHOLE. A PORTION OF THE SANITARY LINE IS LOCATED BELOW THE SCOUR D/S OF MANHOLE (PIN 1). SCOUR DIMENSIONS: 14 M LENGTH, 0.64 M HEIGHT AND 0.4 M WIDTH. THE DEPTH OF COVER ABOVE THE SANITARY LINE IS 2.9 M AT THE SHALLOWEST POINT. LOW PRIORITY ASSIGNED THE 2012 SURVEYED DEPTH OF COVER IS MORE THAN 2 M IN AREA OF ENCROACHMENT. | 0.9 | 2 | 1.9 | 630834 | 4852520 | 630833 | 4852492 | 630837 | 4852513 | Scheduled
2014 | P-065 | Markham | Don River | German Mills Creek (DR) | 2014-08-12 | 10:31 | 11:08 | JS | OT | Proximity | Sanitary Main (Gravity) | MHLC182 -MHLC183 | 630838 | 4852504 | LESLIE STREET | STEELES AVENUE WEST | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, AND FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years | SL | Active |  | No |  |  |  | No | 9.1 | -0.85 | Estimated |  | 57 | Gravel (2 - 64 mm) | Rip Rap | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Gabion Basket | 91-100 | Mixed |  |  |  | 0.64 | N | U | A | N | No | No | No | No | No | No | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR | POST-STORM INSPECTION. NO CHANGES IN STATION DISTANCES OR BANK CONDITIONS IN AREA OF ENCROACHMENT. PRIORITY REMAINS LOW AS THE 2012 SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 2.9 M. | 0.9 | 2 | 1.9 | 630834 | 4852520 | 630833 | 4852492 | 630837 | 4852513 | Scheduled
2016 | P-065 | Markham | Don River | German Mills Creek (DR) | 2016-06-13 | 9:52 | 10:45 | KY | JDa | Proximity | Sanitary Main (Gravity) | MHLC182 -MHLC183 | 630838 | 4852504 | LESLIE STREET | STEELES AVENUE WEST | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, AND FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years | NB | Active |  | No |  | 2.87 | 2016-06-13 | No | 9.1 | -0.9 | Estimated |  | 57 | Gravel (2 - 64 mm) | Sand (< 2mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | N/A | Mixed | 7.7 | 1.47 | 5.24 | 0.39 | N | U&D | A | D | Yes | No | No | No | No | No | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR & DISPLACEMENT | THE TOP OF LEFT BANK IS ERODING ABOVE THE RIP RAP REVETMENT NEAR THE SANITARY MANHOLE. A PORTION OF THE SANITARY LINE IS LOCATED BELOW THE SCOUR D/S OF MANHOLE (PIN 1). SCOUR DIMENSIONS: 14 M LENGTH, 0.64 M HEIGHT AND 0.4 M WIDTH. MINOR UNDERCUTTING PRESENT D/S OF THE SCOUR IN FRONT OF THE REVETMENT (DEPTH: 0.29) THE DEPTH OF COVER ABOVE THE SANITARY LINE IS 2.9 M AT THE SHALLOWEST POINT. THERE IS DOWNCUTTING PRESENT U/S OF PIN 2 IN FRONT OF THE REVETMENT (DEPTH 0.63 M). LOW PRIORITY ASSIGNED AS THE 2012 SURVEYED DEPTH OF COVER IS MORE THAN 2 M IN AREA OF ENCROACHMENT. | 1.3 | 2 | 1.4 | 630834 | 4852520 | 630833 | 4852492 | 630837 | 4852513 | Scheduled
2018 | P-065 | Markham | Don River | German Mills Creek (DR) | 2018-06-05 | 11:07 | 11:22 | HC | OT | Proximity | Sanitary Main (Gravity) | MHLC182 -MHLC183 | 630838 | 4852504 | LESLIE STREET | STEELES AVENUE WEST | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, AND FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years |  | Active |  | No |  |  |  | No | 9.1 | -0.9 | Estimated |  |  | Gravel (2 - 64 mm) | Sand (< 2mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | 91-100 | Mixed | 8.7 | 1.1 | 7.91 | 0.3 | N | A | A | N | No | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes | BANK SCOUR | PIN 2 HAS BEEN DECOMMISSIONED. THE TOP OF LEFT BANK IS ERODING ABOVE THE RIP RAP REVETMENT NEAR THE SANITARY MANHOLE. MINOR DISPLACEMENT OF RIP RAP REVETMENT AT THE D/S PORTION. MINOR DEBRIS BUILDUP AT THE D/S LIMIT OF THE SCOUR. A PORTION OF THE SANITARY LINE IS LOCATED BELOW THE SCOUR D/S OF MANHOLE (PIN 1). LEFT BANK IS SCOURING A HIGH FLOW BEHIND THE REVETMENT, HOWEVER, THE U/S PORTION OF THE SCOUR HAS RE-VEGETATED SOME SINCE THE LAST INSPECTION. (SCOUR DIMENSIONS: 7.5 M LENGTH, 0.7 M HEIGHT AND 0.4 M WIDTH). THE DEPTH OF COVER ABOVE THE SANITARY LINE IS 2.9 M AT THE SHALLOWEST POINT. LOW PRIORITY ASSIGNED AS THE 2012 SURVEYED DEPTH OF COVER IS MORE THAN 2 M IN AREA OF ENCROACHMENT. | 1.3 |  | 1.4 | 630834 | 4852520 | 630833 | 4852492 | 630837 | 4852513 | Scheduled
2021 | P-065 | Markham | Don River | German Mills Creek (DR) | 2021-07-14 | 12:00 | 12:30 | NPa | SV | Proximity | Sanitary Main (Gravity) | MHLC182 -MHLC183 | 630838 | 4852504 | LESLIE STREET | STEELES AVENUE WEST | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, AND FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years |  | Active |  | No |  |  |  | No | 9.1 | -0.9 | Estimated |  |  | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Densely Vegetated | 61-90 | Mixed |  |  |  |  | N | U | A | U | No | No | No | No | No | No | No | No | No | No | No | No | No | No |  | Bank conditions have improved following revegetation but the distance of the Pins to the top of the bank have changed since the 2018 inspection. The sanitary main (gravity) parallels the left bank along an outer meander. Staff suspect difference in Pin distance to top of bank is the result of surface run-off. The scour mentioned previously behind the rip rap revetment has revegetated however the crest is still visible towards the u/s limit of the site. Moderate displaced of rip rap has occurred in the area adjacent to Pin 3. Minor to moderate debris buildup is evident throughout the site, up-slope of the revetment. |  |  |  | 630834 | 4852520 | 630833 | 4852492 | 630837 | 4852513 | Scheduled
2023 | P-065 | Markham | Don River | German Mills Creek (DR) | 2023-07-06 | 12:03 | 12:22 | KLa | ALo | Proximity | Sanitary Main (Gravity) | MHLC182 -MHLC183 | 630838 | 4852504 | LESLIE STREET | STEELES AVENUE WEST | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, AND FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 1 |  | Every 2 Years |  | Active |  | No |  |  |  | No | 9.1 | -0.9 | Estimated |  |  | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Silt | 0-30 | N/A | 15.8 | 1.54 | 10.26 | 0.19 | N | D | U&D | A | Yes | No | No | No | No | Yes | No | Yes | Yes | No | No | No | No | No |  | Moderate changes have occurred at the site since the pervious inspections. The sanitary main (gravity) parallels the left bank along an outer meander. Only a portion of the scour is evident at the u/s limit of the site and measures 10.2 m in length, 2.15 m in width and 0.97 m in height and coir netting and staking's are present throughout the area of the scour. The cobble stone revetment along the left bank is still in good condition with sediment buildup at the d/s limit of the structure. A sediment bar has formed at the d/s limit of the site and downcutting of 0.28 m is present adjacent to the bar. Water seepage appears to occurring at the d/s area of the sediment bar. |  |  |  | 630834 | 4852520 | 630833 | 4852492 | 630837 | 4852513 | Scheduled
2012 | P-065 | Markham | Don River | German Mills Creek (DR) | 2012-06-26 | 14:01 | 2:10 | CP | MJ | Proximity | Sanitary Main (Gravity) | MHLC182 -MHLC183 | 630838 | 4852504 | LESLIE STREET | STEELES AVENUE WEST | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, AND FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years | DC | Active |  | Yes |  | 2.87 |  | No | 9.1 | -0.85 | Surveyed | 2012-07-17 | 56 | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | N/A | 61-90 | Grasses/Forbs | 11.8 | 1.75 | 6.74 | 0.75 | N | A | A | D | No | No | No | Yes | No | No | No | No | No | Yes | Yes | No | No | No |  | P-064 AND P-066 HAVE BEEN MERGED WITH P-065. PIN 1 FORMERLY PIN 1 OF P-064; PIN 2 FORMERLY PIN 1 OF P-066. A PORTION OF THE SANITARY LINE IS LOCATED BELOW THE LEFT BANK SCOUR NEAR THE SANITARY MANHOLE (PIN 1). THE BANK IS SCOURING ABOVE THE RIP RAP REVETMENT. THE SURVEYED DEPTH OF COVER OF THE ENCROACHED LINE BELOW THE SCOUR IS 2.9 M. MINOR UNDERCUTTING ALONG SCOUR AT HIGH FLOW AND DISPLACEMENT OF RIP RAP ON BANK. DEBRIS BUILDUP HAS FORMED AT THE U/S LIMIT OF THE MEANDER. SOME TREES ARE LEANING IN THE D/S AREA OF THE PROXIMITY SITE. THE PEDESTRIAN PATH IS LOCATED 2.5 M FROM THE SCOUR AT THE CLOSEST POINT. LOW PRIORITY ASSIGNED AS ALTHOUGH THE INFRASTRUCTURE IS ENCROACHED BELOW THE BANK THERE IS CURRENTLY 2.9 M OF COVER ABOVE SANITARY MAIN AND THE SCOUR IS MINOR. | 1 | 2 |  | 630834 | 4852520 | 630833 | 4852492 | 630837 | 4852513 | Scheduled
2011 | P-065 | Markham | Don River | German Mills Creek (DR) | 2011-08-11 | 12:52 | 13:11 | MJ | SL | Proximity | Sanitary Main (Gravity) | MHLC182 -MHLC183 | 630838 | 4852504 | LESLIE STREET | STEELES AVENUE WEST | ASK FOR PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, AND FOLLOW WATERCOURSE U/S TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  |  |  |  | 2 |  | Every 2 Years | DC | Active |  | No |  |  |  | No | 9.1 | 1 |  |  | 56 | Sand (< 2mm) | Cobbles (64 - 256 mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Cobbles (64 - 256 mm) | 61-90 | Grasses/Forbs | 8.4 | 1.98 | 4.24 | 0.79 | N | A | U&D | N | No | No | No | No | No | No | No | No | No | Yes | Yes | Yes | No | No |  | PIN 1 IS THE EDGE OF THE FORMAL PATH RUNNING PARALLEL TO THE WATERCOURSE. THE SANITARY MAIN RUNS PARALLEL TO THE LEFT BANK ON AN OUTER MEANDER. THERE IS 14 M OF MINOR SCOURING IS PRESENT ON THE BANK. CUTTING IS OCCURING AT HIGH FLOW ONLY AND IS FAIRLY MINOR. A DEBRIS JAM HAS FORMED AT THE U/S END OF THE MEANDER. SOME TREES ARE LEANING IN THE D/S AREA OF THE PROXIMITY SITE. LOW PRIORITY AS THE MAJORITY OF THE BANK ADJACENT TO THE INFRASTRUCTURE APPEARS STABLE. THE ALIGNMENT OF THE WATERCOURSE ON THE AS-BUILT IS DIFFERENT THAN THE CURRENT POSITIONING, THEREFORE CURRENT DISTANCE TO INFRASTRUCTURE IS NOT KNOWN. | 2.5 |  |  | 630834 | 4852520 | 630833 | 4852492 | 630837 | 4852513 | Scheduled
2011 | P-068 | Markham | Don River | German Mills Creek (DR) | 2011-08-11 | 8:59 | 10:09 | MJ | SL | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually | DC | Active |  | Yes | 3.4 |  |  | No | 9.4 | -2 |  |  | 52 | Sand (< 2mm) | Rip Rap | Rip Rap | Armourstone | Sand (< 2mm) | N/A | 91-100 | Grasses/Forbs | 7.4 | 1.4 | 5.29 | 0.86 | N | A | A | U&D | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No |  | THE SANITARY MAIN APPEARS TO CROSS THROUGH THE CHANNEL D/S OF THE FOOTBRIDGE. BED MATERIAL PRIMARILY CONSISTS OF SAND WITH SOME RIP RAP PRESENT ALONG THE LEFT BANK. THE MANHOLE IS PROTECTED BY AN ARMOURSTONE RETAINING WALL. THE BED ALONG THE OUTER MEANDER IS DOWNCUTTING. THE ALIGNMENT OF THE WATECOURSE ON THE AS-BUILT DRAWING IS DIFFERENT THAN CURRENT ALIGNMENT. HIGH PRIORITY AS INFRASTRUCTURE MAY NOW BE LOCATED BENEATH THE CHANNEL BED AND DEPTH OF COVER IS NOT KNOWN. |  |  |  | 630852 | 4852463 |  |  |  |  | Scheduled
2012 | P-068 | Markham | Don River | German Mills Creek (DR) | 2012-06-22 | 11:08 | 0:00 | MK | RP | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually | DC | Active |  | Yes | 3.4 | 1.31 |  | No | 9.4 | -6.78 | Surveyed | 2012-04-16 | 49 | Sand (< 2mm) | Sand (< 2mm) | Armourstone | Rip Rap | Densely Vegetated | Sand (< 2mm) | 61-90 | Mixed | 8.7 | 1.85 | 4.7 | 0.86 | N | U | N | U&D | No | No | No | No | Yes | No | No | No | No | No | No | No | No | No |  | MAJOR MIGRATION OF THE WATERCOURSE SINCE INSTALLATION OF INFRASTRUCTURE HAS CAUSED THE WATERCOURSE TO MOVE OVER THE SANITARY MAIN. THE DISTANCE FROM THE LEFT BANK TO THE SANITARY MAIN WITHIN THE CHANNEL IS 6.8 M AT THE WIDEST POINT. THE MINIMUM SURVEYED DEPTH OF COVER IS 1.3 M. A RIP RAP REVETMENT ARMOURS THE LEFT BANK ALONG THE OUTSIDE MEANDER; NO DEFICIENCIES OBSERVED. AN ARMOURSTONE RETAINING WALL PROTECTS THE BANK IN AREA OF THE MANHOLE. NO MAJOR DEFICIENCIES OBSERVED FOR RETAINING WALL. THE LEFT BANK IS SCOURING IMMEDIATELY D/S OF THE FOOTBRIDGE. THE SCOUR MEASURES 9 M IN LENGTH, 0.8 M IN WIDTH AND 0.8 IN HEIGHT. THE CHANNEL BED APPEARS TO BE DOWNCUTTING ALONG THE TOE OF THE RIP RAP REVETMENT, ADJACENT TO THE ENCROACHED INFRASTRUCTURE. HIGH PRIORITY ASSIGNED AS WATERCOURSE HAS MOVED OVER THE INFRASTRUCTURE AND ALTHOUGH THE SURVEYED DEPTH OF COVER IS 1.3 M DOWNCUTTING IS EVIDENT ON CHANNEL BED AND LIKELY PROGRESSIVE DUE TO ARMOURED LEFT BANK (OUTER MEANDER) | 2.6 |  |  | 630852 | 4852463 |  |  |  |  | Scheduled
2013 | P-068 | Markham | Don River | German Mills Creek (DR) | 2013-05-22 | 14:36 | 14:47 | CP | MK | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually | SL | Active |  | No | 3.4 |  |  | No | 9.4 | -6.8 | Estimated |  |  | Sand (< 2mm) | Sand (< 2mm) | Armourstone | Rip Rap | Sand (< 2mm) | N/A | 61-90 | Mixed | 8.9 | 1.76 | 5.06 | 0.91 | N | U | N | U&D | Yes | No | No | No | Yes | No | No | No | No | No | No | No | No | Yes | BANK SCOUR | WATERCOURSE HAS MOVED OVER THE INFRASTRUCTURE. BANK ADJACENT TO THE ENCROACHED MAIN HAS BEEN ARMOURED WITH A RIP RAP REVETMENT. SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 1.3 M (2012). SCOUR D/S OF THE FOOTBRIDGE IS REVEGETATING AND APPEARS TO BE STABILIZING; PIN 1 DECOMMISSIONED IN THIS AREA. CHANNEL IS DEEP AND FAST FLOWING ALONG THE TOE OF THE OUTSIDE MEANDER IN AREA OF ENCROACHMENT; MAY BE SUSCEPTIBLE TO DOWNCUTTING AT HIGH FLOW. HIGH PRIORITY ASSIGNED AS WATERCOURSE HAS MOVED OVER THE INFRASTRUCTURE AND DEPTH OF COVER IS 1.3 M OVER THE ENCROACHED MAIN; HIGHER RISK OF EXPOSURE IN AREA OF ENCROACHMENT DUE TO FAST FLOWING WATER AND LACK OF BED PROTECTION. |  |  |  | 630852 | 4852463 |  |  |  |  | Scheduled
2014 | P-068 | Markham | Don River | German Mills Creek (DR) | 2014-07-24 | 10:29 | 11:15 | OT | JS | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually | SL | Active |  | Yes | 3.4 | 0.46 |  | No | 9.4 | -7.66 | Surveyed | 2014-11-13 | 50 | Sand (< 2mm) | Gravel (2 - 64 mm) | Boulders (265mm +) | Rip Rap | Sand (< 2mm) | N/A | 61-90 | Mixed | 9.2 | 1.76 | 5.23 | 0.85 | N | U&D | A | U&D | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No |  | THE WATERCOURSE HAS MIGRATED OVER THE INFRASTRUCTURE. THE 2014 SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.5 M; THIS REPRESENTS A SIGNIFICANT DECREASE FROM 1.3 M AS SURVEYED IN 2012. REVETMENT ARMOURING THE OUTSIDE MEANDER IS IN GOOD CONDITION. CHANNEL IS DOWNCUTTING ALONG THE BED IN AREA OF ENCROACHMENT. SCOUR U/S OF THE REVETMENT IS REVEGETATING AND APPEARS TO BE STABILIZING. HIGH PRIORITY ASSIGNED AS A SECTION OF THE SANITARY MAIN IS ENCROACHED WITH A CURRENT DEPTH OF COVER OF 0.5 M; SANITARY LINE IS NOT ENCASED IN AREA OF ENCROACHMENT BASED ON THE AS-BUILT. |  |  |  | 630852 | 4852463 |  |  |  |  | Scheduled
2015 | P-068 | Markham | Don River | German Mills Creek (DR) | 2015-05-19 | 13:07 | 13:28 | OT | DM | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually | SL | Active |  | No | 3.4 | 0.72 |  | No | 9.4 | -7.7 | Surveyed | 2015-10-20 | 50 | Sand (< 2mm) | Gabion Basket | Armourstone | Rip Rap | Sand (< 2mm) | N/A | 31-60 | Mixed | 6.8 | 1.29 | 5.27 | 0.44 | N | N | A | U | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No |  | THE WATERCOURSE HAS MIGRATED OVER THE INFRASTRUCTURE. THE 2015 SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.7 M. THE RIP RAP REVETMENT ARMOURING THE OUTSIDE MEANDER IS IN GOOD CONDITION. THE CHANNEL BED IS DOWNCUTTING IN AREA OF ENCROACHMENT. SCOUR U/S OF THE REVETMENT IS REVEGETATING AND APPEARS TO BE STABILIZING. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED WITH A CURRENT DEPTH OF COVER OF 0.7 M; THE SANITARY MAIN AT THIS SITE IS NOT ENCASED BASED ON THE AS-BUILT. | 0.8 |  |  | 630852 | 4852463 |  |  |  |  | Scheduled
2016 | P-068 | Markham | Don River | German Mills Creek (DR) | 2016-06-13 | 11:04 | 11:41 | KY | JDa | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually | SL | Active |  | No | 3.4 |  |  | No | 9.4 | -7.7 | Estimated |  |  | Gravel (2 - 64 mm) | Sand (< 2mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | 31-60 | Mixed | 9.7 | 1.11 | 8.74 | 0.11 | N | U | U&D | A | Yes | No | Yes | No | No | No | No | No | No | Yes | No | No | No | Yes | BANK SCOUR & EXPOSED GEOTEXTILE | THE WATERCOURSE HAS MIGRATED OVER THE INFRASTRUCTURE. THE 2015 SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.7 M. THE RIP RAP REVETMENT ARMOURING THE OUTSIDE MEANDER IS IN GOOD CONDITION AT PRESENT. THE CHANNEL BED IS DOWNCUTTING IN AREA OF ENCROACHMENT. SCOUR U/S OF THE REVETMENT APPEARS TO BE REVEGETATING AND STABILIZING. EXPOSED GEOTEXTILE IS PRESENT ON THE LEFT BANK IMMEDIATELY D/S OF THE FOOTBRIDGE. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED WITH A DEPTH OF COVER OF 0.7 M AS OF 2015. | 0.8 |  |  | 630852 | 4852463 |  |  |  |  | Scheduled
2017 | P-068 | Markham | Don River | German Mills Creek (DR) | 2017-05-30 | 9:42 | 10:10 | KY | OT | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually | JSP | Active |  | No | 3.4 |  |  | No | 9.4 | -7.7 | Estimated |  | 46 | Gravel (2 - 64 mm) | Sand (< 2mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Gabion Basket | 61-90 | Mixed | 5.5 | 1.2 | 4.58 | 0.29 | N | U | A | U&D | Yes | No | Yes | No | No | No | No | No | No | Yes | Yes | No | No | Yes | BANK SCOUR & EXPOSED GEOTEXTILE | THE WATERCOURSE HAS MIGRATED OVER THE INFRASTRUCTURE LEAVING SANITARY MAIN ENCROACHED BY 7.7 M. THE 2015 SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.7 M. THE RIP RAP REVETMENT ARMOURING THE OUTSIDE MEANDER IS IN GOOD CONDITION AT PRESENT, HOWEVER THERE IS UNDERCUTTING AT THE CREST WITH A DEPTH OF 0.3 M. THE CHANNEL BED IS DOWNCUTTING IN AREA OF ENCROACHMENT (WATER LEVEL: >1.3 M). SCOUR U/S OF THE REVETMENT APPEARS TO BE REVEGETATING AND STABILIZING. EXPOSED GEOTEXTILE IS PRESENT ON THE RIGHT BANK IMMEDIATELY D/S OF THE FOOTBRIDGE. A FAILED TREE IS CROSSING THE WATERCOURSE IMMEDIATELY D/S OF PIN 1 (MANHOLE). HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED WITH A DEPTH OF COVER OF 0.7 M AS OF 2015. | 0.8 |  |  | 630852 | 4852463 |  |  |  |  | Scheduled
2017 | P-068 | Markham | Don River | German Mills Creek (DR) | 2017-06-27 | 12:41 | 13:00 | OT | KY | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually | JSP | Active |  | No | 3.4 |  |  | No | 9.4 | -7.7 | Estimated |  | 46 | [31 empty] | **POST STORM INSPECTION: NO MAJOR CHANGE SINCE LAST INSPECTION. SEE PREVIOUS INSPECTION FOR COMMENTS. | 0.8 |  |  | 630852 | 4852463 | bar: Yes to No
2018 | P-068 | Markham | Don River | German Mills Creek (DR) | 2018-04-05 | 12:45 | 13:20 | OT | RC | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually |  | Active |  | No | 3.4 |  |  | No | 9.4 | -7.7 | Estimated |  | 48 | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | 61-90 | Mixed |  |  |  |  | N | U | A | U&D | Yes | No | No | No | No | No | No | No | No | No | No | No | No | Yes | SETTLEMENT | POST STORM INSPECTION, HIGH WATER LEVELS OBSERVED SO CHANNEL DIMENSIONS WERE NOT COMPLETED. THE WATERCOURSE HAS MIGRATED OVER THE INFRASTRUCTURE LEAVING SANITARY MAIN ENCROACHED BY 7.7 M. THE 2015 SURVEYED DEPTH OF COVER OVER THE ENCROACHED MAIN IS 0.7 M. THE RIP RAP REVETMENT ARMOURING THE OUTSIDE MEANDER IS IN GOOD CONDITION AT PRESENT, HOWEVER IT APPEARS THE RIP RAP HAVE SETTLED INTO THE BANK. THE CHANNEL BED IS DOWNCUTTING IN AREA OF ENCROACHMENT (WATER LEVEL: >1.3 M). SCOUR U/S OF THE REVETMENT APPEARS TO BE REVEGETATING AND STABILIZING. EXPOSED GEOTEXTILE IS PRESENT ON THE RIGHT BANK IMMEDIATELY D/S OF THE FOOTBRIDGE. THE ARMOURSTONE ARMOURING THE BANK ADJACENT TO THE MANHOLE (PIN 1) APPEARS TO HAVE SETTLED TOWARDS THE BANK. A FAILED TREE IS CROSSING THE WATERCOURSE IMMEDIATELY D/S OF PIN 1 (MANHOLE). HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED WITH A DEPTH OF COVER OF 0.7 M AS OF 2015. | 0.8 |  |  | 630852 | 4852463 |  |  |  |  | Scheduled
2018 | P-068 | Markham | Don River | German Mills Creek (DR) | 2018-07-19 | 13:12 | 13:20 | TY | OT | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually |  | Active |  | No | 3.4 |  |  | No | 9.4 | -7.7 | Estimated |  |  | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Densely Vegetated | Sand (< 2mm) | Gravel (2 - 64 mm) | 31-60 | Mixed | 7.7 | 1.59 | 4.84 | 0.83 | N | D | A | U&D | Yes | No | No | No | No | No | No | No | No | No | Yes | No | No | Yes | DEBRIS BUILDUP | **POST STORM INSPECTION** NO MAJOR CHANGES OBSERVED SINCE PREVIOUS INSPECTION. THE WATERCOURSE HAS MIGRATED OVER THE SANITARY MAIN AND IS ENCROACHED BY 7.7 M. THE 2015 SURVEYED DEPTH OF COVER OVER THE ENCROACHMENT IS 0.7 M. THE MANHOLE CHIMNEY IS EXPOSED WITH HEIGHT 0.57 M. THE RIP RAP REVETMENT ARMOURING THE OUTER MEANDER IS IN GOOD CONDITION, HOWEVER SOME OF THE RIP RAP APPEARS TO HAVE SETTLED INTO THE BANK. THE CHANNEL BED IS DOWNCUTTING IN AREA OF ENCROACHMENT (WATER LEVEL : 1.15 M). ARMOUR STONES ADJACENT TO THE MANHOLE (PIN 1) APPEARS TO HAVE SETTLED TOWARDS THE BANK. A FAILED TREE IS CROSSING THE WATERCOURSE IMMEDIATELY D/S OF PIN 1 (MANHOLE). MINOR WOODY DEBRIS BUILD UP U/S OF THE FALLEN TREE. SEDIMENT BAR IS FOUND IN THE D/S SECTION ON THE RIGHT BANK. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED WITH A DEPTH OF COVER OF 0.7 M AS OF 2015. | 0.8 |  |  | 630852 | 4852463 |  |  |  |  | Scheduled
2020 | P-068 | Markham | Don River | German Mills Creek (DR) | 2020-06-15 | 8:30 | 8:42 | CM | NPa | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually |  | Active |  | No | 3.4 | 0.65 | 2018-05-30 | No | 9.4 | -6.67 | Surveyed | 2018-05-30 | 49 | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Densely Vegetated | Sand (< 2mm) | Silt | 91-100 | Shrubs | 10.5 | 2 | 5.25 | 0.3 | N | D | D | U | Yes | No | No | Yes | No | No | No | No | No | No | No | No | No | Yes | Displacement | The watercourse has migrated over the sanitary main and is encroached by 6.67 m with 0.65 of remaining cover over the sanitary main as surveyed in 2018. No change was observed adjacent to the monitoring pin(s) since the previous inspection as the manhole is still 0.7 m from the top of the bank at the closest location. The manhole and d/s portion of the outer meander is being protected by an armourstone retaining wall. The u/s portion of the meander is protected with a rip rap revetment that is in good condition with minor displacement along the u/s and d/s portions; rip rap stones have settled into the bank. The channel bed is down cutting (0.6 m) in the area of encroachment. Significant sand deposition is occurring on the inner meander adjacent to the right bank. The failed tree d/s of the manhole mention during the previous inspection is no long visible at the time of inspection. | 0.7 |  |  | 630852 | 4852463
2021 | P-068 | Markham | Don River | German Mills Creek (DR) | 2021-07-15 | 12:30 | 13:00 | NPa | SV | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually | DL | Active |  | No | 3.4 | 0.65 | 2018-05-30 | No | 9.4 | -6.67 | Surveyed | 2018-05-30 |  | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Silt | 61-90 | Mixed | 10 | 2 | 5 | 0.25 | N | D | A | U | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No |  | No changes observed in the bank conditions or in the distance of Pin 1 to the top of the bank from the previous inspection. The sanitary main parallels the left bank at an outer meander, however, the watercourse has encroached the line by 6.67 m with a depth of cover of 0.65 m as surveyed in 2018. The manhole and d/s portion of the outer meander is being protected by an armourstone retaining wall. The u/s portion of the meander is protected with a rip rap revetment that is in good condition with minor displacement along the u/s and d/s portions. The channel is downcutting in the area of encroachment by 1.0 m. |  |  |  | 630852 | 4852463
2022 | P-068 | Markham | Don River | German Mills Creek (DR) | 2022-06-01 | 8:30 | 8:45 | AP | LS | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually |  | Active |  | No | 3.4 | 0.65 | 2018-05-30 | No | 9.4 | -6.67 | Surveyed | 2018-05-30 |  | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Silt | 61-90 | Mixed | 9.8 | 1.38 | 7.1 | 0.14 | N |  | A |  | Yes | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | Displacement and toe erosion | Minor changes have occurred at the site since the previous inspection. The sanitary main parallels the left bank at an outer meander, however, the watercourse has encroached the line by 6.67 m with a depth of cover of 0.65 m as surveyed in 2018. The manhole and d/s portion of the outer meander is being protected by an armourstone retaining wall. The u/s portion of the meander is protected with a rip rap revetment that is in good condition with minor displacement along the u/s and d/s portions. The measurement for Pin 1 remains the same at 0.7 m from the manhole to the end of the armourstone retaining wall. The channel is still downcutting in the area of encroachment by 1.0 m. The right bank is now experiencing minor slumping with tension cracks throughout the inner meander. The previously reported undercut on the left bank along the rip rap revetement has increased from 0.3 to 0.4 m since the previous inspection. Sediment buildup and pooling is also found along the left bank in the areas of rip rap displacement. Minor toe erosion is found at the d/s limit of the site along the right bank. |  |  |  | 630852 | 4852463
2023 | P-068 | Markham | Don River | German Mills Creek (DR) | 2023-07-07 | 10:53 | 11:13 | ALo | KLa | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 1 |  | Annually |  | Active |  | No | 3.4 | 0.65 | 2018-05-30 | No | 9.4 | -6.67 | Surveyed | 2018-05-30 |  | Sand (< 2mm) | Silt | Cobbles (64 - 256 mm) | Armourstone | Cobbles (64 - 256 mm) | Silt | 31-60 | Grasses/Forbs | 18.3 | 0.81 | 22.59 | 0.39 | N | N | A | U&D | Yes | No | No | No | No | No | No | No | No | Yes | No | No | No | Yes | Spalling | Changes have occurred to site conditions since previous inspection as restoration works were completed on site. The sanitary main (gravity) parallels the left bank at an outer meander but is no longer encroached. The distance of Pin 1 (manhole) to the bank has remained the same. Root wads are present at the midsection of the site on the left bank. Manhole is present in the d/s portion of the site on the left bank and is being protected by an armourstone retaining wall and a cobblestone revetment that spans across the entire site. Exposed coir netting can be found on top of armourstone and throughout the site on the left bank. Vegetation is coming through spaces in cobblestone revetment. U/S of the manhole adjacent to left bank downcutting is occurring measuring 0.71 m. An outfall present at the d/s limit of the site on the left bank. Debris is partially blocking the gate of the outfall. Spalling is present throughout the spillway and right wingwall. Bank is well vegetated and appears stable at time of inspection. Toe erosion on right bank is no longer present. |  |  |  | 630852 | 4852463
2018 | P-068 | Markham | Don River | German Mills Creek (DR) | 2018-08-07 | 11:08 | 11:19 | HC | OT | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually |  | Active |  | No | 3.4 |  |  | No | 9.4 | -6.7 | Surveyed | 2018-05-30 | 48 | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Densely Vegetated | Sand (< 2mm) | Gravel (2 - 64 mm) | 31-60 | Mixed |  |  |  |  | N | D | A | U&D | Yes | No | No | No | No | No | No | No | No | No | Yes | No | No | Yes | DEBRIS BUILDUP & EXPOSED CHIMNEY | **POST STORM INSPECTION** NO MAJOR CHANGES OBSERVED SINCE PREVIOUS INSPECTION. CHANNEL MEASUREMENTS WERE NOT TAKEN AT THIS TIME AS THE WATER LEVELS WERE TOO HIGH. THE WATERCOURSE HAS MIGRATED OVER THE SANITARY MAIN AND IS ENCROACHED BY 7.7 M. THE 2015 SURVEYED DEPTH OF COVER OVER THE ENCROACHMENT IS 0.7 M. THE MANHOLE CHIMNEY IS EXPOSED WITH HEIGHT OF 0.65 M. THE RIP RAP REVETMENT ARMOURING THE OUTER MEANDER IS IN GOOD CONDITION, HOWEVER SOME OF THE RIP RAP APPEARS TO HAVE SETTLED INTO THE BANK. THE CHANNEL BED IS DOWNCUTTING IN AREA OF ENCROACHMENT BUT WATER LEVELS WERE NOT TAKEN AT THIS TIME. ARMOUR STONES ADJACENT TO THE MANHOLE (PIN 1) APPEARS TO HAVE SETTLED TOWARDS THE BANK. A FAILED TREE IS CROSSING THE WATERCOURSE IMMEDIATELY D/S OF PIN 1 (MANHOLE). MINOR WOODY DEBRIS BUILD UP HAS OCCURRED IMMEDIATELY U/S OF THE FAILED TREE. A SEDIMENT BAR IS FOUND IN THE D/S SECTION ON THE RIGHT BANK. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED WITH A DEPTH OF COVER OF 0.7 M AS OF 2015. | 0.7 |  |  | 630852 | 4852463
2019 | P-068 | Markham | Don River | German Mills Creek (DR) | 2019-05-28 | 12:20 | 12:45 | SK | SD | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually |  | Active |  | No | 3.4 |  |  | No | 9.4 |  |  |  | 46 | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Densely Vegetated | Sand (< 2mm) | Gravel (2 - 64 mm) | 91-100 | Mixed |  |  |  |  | N | D | A | U&D | Yes | No | No | No | No | No | No | No | No | No | Yes | No | No | Yes | debris build up, exposed chimney | Channel measurements were not taken at this time as the water levels were too high. The watercourse has migrated over the sanitary main and is encroached by 6.67 m. The 2018 surveyed depth of cover over the encroachment is 0.65 m. The manhole chimney is exposed with height of 0.65 m. The rip rap revetment armouring the outer meander is in good condition, however some of the rip rap appears to have settled into the bank. The channel bed is downcutting in area of encroachment but water levels were not taken at this time. Armour stones adjacent to the manhole (pin 1) appears to have settled towards the bank. A failed tree is crossing the watercourse immediately d/s of pin 1 (manhole). Minor woody debris build up has occurred immediately u/s of the failed tree. A sediment bar is found in the d/s section on the right bank. High priority assigned as the sanitary main is encroached with a depth of cover of 0.65 m as of 2018. | 0.7 |  |  | 630852 | 4852463
2018 | P-068 | Markham | Don River | German Mills Creek (DR) | 2018-04-18 | 11:00 | 11:10 | OT | DG | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually |  | Active |  | No | 3.4 |  |  | No | 9.4 | -7.7 | Estimated |  | 48 | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Sand (< 2mm) | Sand (< 2mm) | Gravel (2 - 64 mm) | 0-30 | Mixed |  |  |  |  | N | N | A | U&D | Yes | No | No | No | No | No | No | No | No | No | No | No | No | Yes | SETTLEMENT | POST STORM INSPECTION, NO CHANGES OBSERVED SINCE PREVIOUS INSPECTION. THE WATERCOURSE HAS MIGRATED OVER THE SANITARY MAIN AND IS ENCROACHED BY 7.7 M. THE 2015 SURVEYED DEPTH OF COVER OVER THE ENCROACHMENT IS 0.7 M. THE RIP RAP REVETMENT ARMOURING THE OUTER MEANDER IS IN GOOD CONDITION, HOWEVER SOME OF THE RIP RAP APPEARS TO HAVE SETTLED INTO THE BANK. THE CHANNEL BED IS DOWNCUTTING IN AREA OF ENCROACHMENT (WATER LEVEL: >1.3 M). ARMOURSTONES ADJACENT TO THE MANHOLE (PIN 1) APPEARS TO HAVE SETTLED TOWARDS THE BANK. A FAILED TREE IS CROSSING THE WATERCOURSE IMMEDIATELY D/S OF PIN 1 (MANHOLE). HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED WITH A DEPTH OF COVER OF 0.7 M AS OF 2015. | 0.8 |  |  | 630852 | 4852463
2018 | P-068 | Markham | Don River | German Mills Creek (DR) | 2018-07-10 | 12:18 | 12:40 | HC | OT | Proximity | Sanitary Main (Gravity) | MHLC183 -MHLC184 | 630855.91 | 4852450.07 | LESLIE STREET | STEELES AVENUE WEST | ASK PERMISSION TO PARK AT ADVENTURE VALLEY DAY CAMP, THEN WALK U/S ALONG WATERCOURSE TO SITE. | City of Markham | Cashel Clay | Clay |  |  | WW-LC-007 | LC |  | Yes | 7 | Included in the geomorphic assessment of Settlers Park completed in 2015. | 4 |  | Annually |  | Active |  | No | 3.4 |  |  | No | 9.4 | -7.7 | Estimated |  | 48 | Sand (< 2mm) | Gravel (2 - 64 mm) | Rip Rap | Densely Vegetated | Sand (< 2mm) | Gravel (2 - 64 mm) | 31-60 | Mixed | 7.7 | 1.4 | 5.5 | 0.49 | N | D | A | U&D | Yes | No | No | No | No | No | No | No | No | No | Yes | No | No | No |  | **POST STORM INSPECTION** NO MAJOR CHANGES OBSERVED SINCE PREVIOUS INSPECTION. THE WATERCOURSE HAS MIGRATED OVER THE SANITARY MAIN AND IS ENCROACHED BY 7.7 M. THE 2015 SURVEYED DEPTH OF COVER OVER THE ENCROACHMENT IS 0.7 M. THE RIP RAP REVETMENT ARMOURING THE OUTER MEANDER IS IN GOOD CONDITION, HOWEVER SOME OF THE RIP RAP APPEARS TO HAVE SETTLED INTO THE BANK. THE CHANNEL BED IS DOWNCUTTING IN AREA OF ENCROACHMENT (WATER LEVEL : 0.87 M). ARMOURSTONES ADJACENT TO THE MANHOLE (PIN 1) APPEARS TO HAVE SETTLED TOWARDS THE BANK. A FAILED TREE IS CROSSING THE WATERCOURSE IMMEDIATELY D/S OF PIN 1 (MANHOLE). SEDIMENT BAR IS FOUND IN THE D/S SECTION ON THE RIGHT BANK. HIGH PRIORITY ASSIGNED AS THE SANITARY MAIN IS ENCROACHED WITH A DEPTH OF COVER OF 0.7 M AS OF 2015. | 0.8 |  |  | 630852 | 4852463 |  |  |  |  | Scheduled